## Sheet1
Duct Pressure Loss Report
Project Name
Project Issue Date
Project Status
Client Name
Project Address
Project Number
Organization Name
Organization Description
Building Name
Author
IfcSite GUID | 06dWEt2jDAexxjgLznnrNn
IfcBuilding GUID | 06dWEt2jDAexxjgLznnrNo
IfcProject GUID | 06dWEt2jDAexxjgLznnrNp
Document GUID
SR Document GUID
PrintManagerSettings
SiteName
AreaCalculationInternationalOptions
ADSK_DICTIONARY_AREA_CALCULATION_TYPE
AreaCalculationInternationalBuildNumber
RoomBookInternationalBuildNumber
BuildingbookInternationalBuildNumber
Run Time | 3/3/2025 5:30:47 PM
L_Abluft 2
System Information
System Classification | Return Air
System Type | Abluft
System Name | L_Abluft 2
Abbreviation | L_Abluft
Total Pressure Loss Calculations by Sections
Section | Element | Flow | Size | Velocity | Velocity Pressure | Length | Loss Coefficient | Friction | Total Pressure Loss | Section Pressure Loss
1 | Duct | 13549.6 CMH | 1850 mmx1160 mm | 1.8 m/s | - | 903 | - | 0.02 Pa/m | 0.019 Pa | 0.019 Pa
| Fittings | 13549.6 CMH | - | 1.8 m/s | 1.850 Pa | - | 0 | - | 0.000 Pa
| Equipment | 13549.6 CMH | - | - | - | - | - | - | 0.000 Pa
2 | Duct | 13549.6 CMH | 1000 mmx1000 mm | 3.8 m/s | - | 23062 | - | 0.13 Pa/m | 3.087 Pa | 35.597 Pa
| Fittings | 13549.6 CMH | - | 3.8 m/s | 8.518 Pa | - | 3.8165 | - | 32.510 Pa
3 | Duct | 250.0 CMH | 250 mmø | 1.4 m/s | - | 190 | - | 0.13 Pa/m | 0.024 Pa | 3.646 Pa
| Fittings | 250.0 CMH | - | 1.4 m/s | 1.203 Pa | - | 3.0095 | - | 3.622 Pa
| Air Terminal | 250.0 CMH | - | - | - | - | - | - | 0.000 Pa
4 | Duct | 500.0 CMH | 250 mmø | 2.8 m/s | - | 4766 | - | 0.44 Pa/m | 2.084 Pa | 186.320 Pa
| Fittings | 500.0 CMH | - | 2.8 m/s | 4.814 Pa | - | 38.2721 | - | 184.236 Pa
5 | Duct | 650.0 CMH | 250 mmø | 3.7 m/s | - | 8296 | - | 0.70 Pa/m | 5.825 Pa | 17.925 Pa
| Fittings | 650.0 CMH | - | 3.7 m/s | 8.135 Pa | - | 1.4873 | - | 12.100 Pa
6 | Duct | 1050.0 CMH | 315 mmø | 3.7 m/s | - | 3279 | - | 0.54 Pa/m | 1.780 Pa | 2.481 Pa
| Fittings | 1050.0 CMH | - | 3.7 m/s | 8.423 Pa | - | 0.0833 | - | 0.702 Pa
7 | Duct | 1200.0 CMH | 315 mmø | 4.3 m/s | - | 13026 | - | 0.69 Pa/m | 9.010 Pa | 162.210 Pa
| Fittings | 1200.0 CMH | - | 4.3 m/s | 11.001 Pa | - | 13.926 | - | 153.200 Pa
8 | Duct | 2050.0 CMH | 350 mmx350 mm | 4.6 m/s | - | 275 | - | 0.71 Pa/m | 0.194 Pa | 0.194 Pa
| Fittings | 2050.0 CMH | - | 4.6 m/s | 12.994 Pa | - | 0 | - | 0.000 Pa
9 | Duct | 2050.0 CMH | 400 mmx400 mm | 3.6 m/s | - | 646 | - | 0.37 Pa/m | 0.238 Pa | 17.756 Pa
| Fittings | 2050.0 CMH | - | 3.6 m/s | 7.617 Pa | - | 2.3 | - | 17.518 Pa
10 | Duct | 2400.0 CMH | 400 mmx400 mm | 4.2 m/s | - | 235 | - | 0.49 Pa/m | 0.115 Pa | 0.115 Pa
| Fittings | 2400.0 CMH | - | 4.2 m/s | 10.439 Pa | - | 0 | - | 0.000 Pa
11 | Duct | 2400.0 CMH | 400 mmx400 mm | 4.2 m/s | - | 6094 | - | 0.49 Pa/m | 2.982 Pa | 40.764 Pa
| Fittings | 2400.0 CMH | - | 4.2 m/s | 10.439 Pa | - | 3.6193 | - | 37.783 Pa
12 | Duct | 2400.0 CMH | 600 mmx600 mm | 1.9 m/s | - | 855 | - | 0.07 Pa/m | 0.059 Pa | 0.059 Pa
| Fittings | 2400.0 CMH | - | 1.9 m/s | 2.062 Pa | - | 0 | - | 0.000 Pa
13 | Duct | 4850.0 CMH | 600 mmx600 mm | 3.7 m/s | - | 2945 | - | 0.25 Pa/m | 0.723 Pa | 1.789 Pa
| Fittings | 4850.0 CMH | - | 3.7 m/s | 8.421 Pa | - | 0.12664 | - | 1.066 Pa
14 | Duct | 4850.0 CMH | 700 mmx700 mm | 2.7 m/s | - | 855 | - | 0.12 Pa/m | 0.099 Pa | 0.099 Pa
| Fittings | 4850.0 CMH | - | 2.7 m/s | 4.546 Pa | - | 0 | - | 0.000 Pa
15 | Duct | 7200.0 CMH | 700 mmx700 mm | 4.1 m/s | - | 7309 | - | 0.24 Pa/m | 1.747 Pa | 30.792 Pa
| Fittings | 7200.0 CMH | - | 4.1 m/s | 10.018 Pa | - | 2.8993 | - | 29.044 Pa
16 | Duct | 7200.0 CMH | 1000 mmx500 mm | 4.0 m/s | - | 11399 | - | 0.24 Pa/m | 2.785 Pa | 46.592 Pa
| Fittings | 7200.0 CMH | - | 4.0 m/s | 9.621 Pa | - | 4.5533 | - | 43.807 Pa
17 | Duct | 7200.0 CMH | 1000 mmx500 mm | 4.0 m/s | - | 958 | - | 0.24 Pa/m | 0.234 Pa | 0.234 Pa
| Fittings | 7200.0 CMH | - | 4.0 m/s | 9.621 Pa | - | 0 | - | 0.000 Pa
18 | Duct | 7200.0 CMH | 1000 mmx500 mm | 4.0 m/s | - | 2030 | - | 0.24 Pa/m | 0.496 Pa | 24.196 Pa
| Fittings | 7200.0 CMH | - | 4.0 m/s | 9.621 Pa | - | 2.4633 | - | 23.700 Pa
19 | Duct | 7200.0 CMH | 1000 mmx1000 mm | 2.0 m/s | - | 1289 | - | 0.04 Pa/m | 0.054 Pa | 0.054 Pa
| Fittings | 7200.0 CMH | - | 2.0 m/s | 2.405 Pa | - | 0 | - | 0.000 Pa
20 | Duct | 100.0 CMH | 160 mmø | 1.4 m/s | - | 1338 | - | 0.21 Pa/m | 0.284 Pa | 183.330 Pa
| Fittings | 100.0 CMH | - | 1.4 m/s | 1.148 Pa | - | 159.4881 | - | 183.046 Pa
| Air Terminal | 100.0 CMH | - | - | - | - | - | - | 0.000 Pa
21 | Duct | 350.0 CMH | 250 mmø | 2.0 m/s | - | 2528 | - | 0.23 Pa/m | 0.583 Pa | 5.725 Pa
| Fittings | 350.0 CMH | - | 2.0 m/s | 2.359 Pa | - | 2.1799 | - | 5.142 Pa
22 | Duct | 500.0 CMH | 250 mmø | 2.8 m/s | - | 2840 | - | 0.44 Pa/m | 1.242 Pa | 152.839 Pa
| Fittings | 500.0 CMH | - | 2.8 m/s | 4.814 Pa | - | 31.4919 | - | 151.598 Pa
23 | Duct | 600.0 CMH | 250 mmø | 3.4 m/s | - | 7686 | - | 0.61 Pa/m | 4.669 Pa | 17.740 Pa
| Fittings | 600.0 CMH | - | 3.4 m/s | 6.932 Pa | - | 1.8857 | - | 13.072 Pa
24 | Duct | 850.0 CMH | 280 mmø | 3.8 m/s | - | 98 | - | 0.66 Pa/m | 0.064 Pa | 1.968 Pa
| Fittings | 850.0 CMH | - | 3.8 m/s | 8.841 Pa | - | 0.21534 | - | 1.904 Pa
25 | Duct | 850.0 CMH | 350 mmx350 mm | 1.9 m/s | - | 193 | - | 0.14 Pa/m | 0.028 Pa | 0.028 Pa
| Fittings | 850.0 CMH | - | 1.9 m/s | 2.234 Pa | - | 0 | - | 0.000 Pa
26 | Duct | 150.0 CMH | 160 mmø | 2.1 m/s | - | 1251 | - | 0.44 Pa/m | 0.546 Pa | 184.926 Pa
| Fittings | 150.0 CMH | - | 2.1 m/s | 2.582 Pa | - | 71.3998 | - | 184.380 Pa
| Air Terminal | 150.0 CMH | - | - | - | - | - | - | 0.000 Pa
27 | Duct | 100.0 CMH | 160 mmø | 1.4 m/s | - | 1334 | - | 0.21 Pa/m | 0.283 Pa | 178.001 Pa
| Fittings | 100.0 CMH | - | 1.4 m/s | 1.148 Pa | - | 154.8458 | - | 177.718 Pa
| Air Terminal | 100.0 CMH | - | - | - | - | - | - | 0.000 Pa
28 | Duct | 250.0 CMH | 250 mmø | 1.4 m/s | - | 1775 | - | 0.13 Pa/m | 0.225 Pa | 7.335 Pa
| Fittings | 250.0 CMH | - | 1.4 m/s | 1.203 Pa | - | 5.9085 | - | 7.111 Pa
| Air Terminal | 250.0 CMH | - | - | - | - | - | - | 0.000 Pa
29 | Duct | 125.0 CMH | 160 mmø | 1.7 m/s | - | 3095 | - | 0.32 Pa/m | 0.976 Pa | 1.776 Pa
| Fittings | 125.0 CMH | - | 1.7 m/s | 1.793 Pa | - | 0.4461 | - | 0.800 Pa
| Air Terminal | 125.0 CMH | - | - | - | - | - | - | 0.000 Pa
30 | Duct | 250.0 CMH | 160 mmø | 3.5 m/s | - | 3723 | - | 1.09 Pa/m | 4.075 Pa | 209.408 Pa
| Fittings | 250.0 CMH | - | 3.5 m/s | 7.173 Pa | - | 28.6251 | - | 205.333 Pa
31 | Fittings | 250.0 CMH | - | 0.0 m/s | 1.203 Pa | - | 0.76641 | - | 0.922 Pa | 0.922 Pa
32 | Duct | 150.0 CMH | 160 mmø | 2.1 m/s | - | 1186 | - | 0.44 Pa/m | 0.518 Pa | 182.354 Pa
| Fittings | 150.0 CMH | - | 2.1 m/s | 2.582 Pa | - | 70.4147 | - | 181.836 Pa
| Air Terminal | 150.0 CMH | - | - | - | - | - | - | 0.000 Pa
33 | Fittings | 125.0 CMH | - | 0.0 m/s | 1.793 Pa | - | 0 | - | 0.000 Pa | 0.000 Pa
| Air Terminal | 125.0 CMH | - | - | - | - | - | - | 0.000 Pa
34 | Duct | 400.0 CMH | 250 mmø | 2.3 m/s | - | 8997 | - | 0.29 Pa/m | 2.635 Pa | 188.965 Pa
| Fittings | 400.0 CMH | - | 2.3 m/s | 3.081 Pa | - | 60.4799 | - | 186.331 Pa
| Air Terminal | 400.0 CMH | - | - | - | - | - | - | 0.000 Pa
35 | Fittings | 400.0 CMH | - | 0.0 m/s | 1.222 Pa | - | 4.799 | - | 5.866 Pa | 5.866 Pa
36 | Duct | 150.0 CMH | 160 mmø | 2.1 m/s | - | 3078 | - | 0.44 Pa/m | 1.344 Pa | 179.996 Pa
| Fittings | 150.0 CMH | - | 2.1 m/s | 2.582 Pa | - | 69.1818 | - | 178.652 Pa
| Air Terminal | 150.0 CMH | - | - | - | - | - | - | 0.000 Pa
37 | Duct | 200.0 CMH | 160 mmø | 2.8 m/s | - | 659 | - | 0.73 Pa/m | 0.483 Pa | 8.969 Pa
| Fittings | 200.0 CMH | - | 2.8 m/s | 4.591 Pa | - | 1.8486 | - | 8.487 Pa
| Air Terminal | 200.0 CMH | - | - | - | - | - | - | 0.000 Pa
38 | Duct | 400.0 CMH | 180 mmø | 4.4 m/s | - | 12456 | - | 1.45 Pa/m | 18.005 Pa | 206.340 Pa
| Fittings | 400.0 CMH | - | 4.4 m/s | 11.464 Pa | - | 16.4281 | - | 188.335 Pa
39 | Fittings | 400.0 CMH | - | 0.0 m/s | 3.081 Pa | - | 1.92 | - | 5.915 Pa | 5.915 Pa
40 | Duct | 800.0 CMH | 250 mmø | 4.5 m/s | - | 6823 | - | 1.02 Pa/m | 6.986 Pa | 10.506 Pa
| Fittings | 800.0 CMH | - | 4.5 m/s | 12.323 Pa | - | 0.28563 | - | 3.520 Pa
41 | Duct | 800.0 CMH | 280 mmø | 3.6 m/s | - | 135 | - | 0.59 Pa/m | 0.079 Pa | 1.381 Pa
| Fittings | 800.0 CMH | - | 3.6 m/s | 7.832 Pa | - | 0.16623 | - | 1.302 Pa
42 | Duct | 950.0 CMH | 280 mmø | 4.3 m/s | - | 14145 | - | 0.80 Pa/m | 11.377 Pa | 16.177 Pa
| Fittings | 950.0 CMH | - | 4.3 m/s | 11.044 Pa | - | 0.43462 | - | 4.800 Pa
43 | Duct | 2100.0 CMH | 400 mmx400 mm | 3.6 m/s | - | 369 | - | 0.38 Pa/m | 0.142 Pa | 18.525 Pa
| Fittings | 2100.0 CMH | - | 3.6 m/s | 7.993 Pa | - | 2.3 | - | 18.383 Pa
44 | Duct | 2100.0 CMH | 400 mmx400 mm | 3.6 m/s | - | 215 | - | 0.38 Pa/m | 0.083 Pa | 0.083 Pa
| Fittings | 2100.0 CMH | - | 3.6 m/s | 7.993 Pa | - | 0 | - | 0.000 Pa
45 | Duct | 2350.0 CMH | 400 mmx400 mm | 4.1 m/s | - | 2563 | - | 0.47 Pa/m | 1.207 Pa | 12.942 Pa
| Fittings | 2350.0 CMH | - | 4.1 m/s | 10.009 Pa | - | 1.1725 | - | 11.736 Pa
46 | Duct | 2350.0 CMH | 450 mmx450 mm | 3.2 m/s | - | 807 | - | 0.27 Pa/m | 0.214 Pa | 7.400 Pa
| Fittings | 2350.0 CMH | - | 3.2 m/s | 6.249 Pa | - | 1.15 | - | 7.186 Pa
47 | Duct | 250.0 CMH | 250 mmø | 1.4 m/s | - | 3040 | - | 0.13 Pa/m | 0.385 Pa | 181.985 Pa
| Fittings | 250.0 CMH | - | 1.4 m/s | 1.203 Pa | - | 150.8978 | - | 181.600 Pa
| Air Terminal | 250.0 CMH | - | - | - | - | - | - | 0.000 Pa
48 | Duct | 2499.8 CMH | 400 mmx400 mm | 4.3 m/s | - | 6237 | - | 0.53 Pa/m | 3.286 Pa | 13.286 Pa
| Fittings | 2499.8 CMH | - | 4.3 m/s | 11.326 Pa | - | 0.88295 | - | 10.000 Pa
49 | Duct | 2499.8 CMH | 400 mmx400 mm | 4.3 m/s | - | 67 | - | 0.53 Pa/m | 0.035 Pa | 0.035 Pa
| Fittings | 2499.8 CMH | - | 4.3 m/s | 11.326 Pa | - | 0 | - | 0.000 Pa
50 | Duct | 4099.8 CMH | 500 mmx500 mm | 4.6 m/s | - | 1920 | - | 0.44 Pa/m | 0.845 Pa | 2.655 Pa
| Fittings | 4099.8 CMH | - | 4.6 m/s | 12.478 Pa | - | 0.1451 | - | 1.810 Pa
51 | Duct | 4099.8 CMH | 600 mmx600 mm | 3.2 m/s | - | 1914 | - | 0.18 Pa/m | 0.345 Pa | 0.345 Pa
| Fittings | 4099.8 CMH | - | 3.2 m/s | 6.017 Pa | - | 0 | - | 0.000 Pa
52 | Duct | 6349.6 CMH | 600 mmx600 mm | 4.9 m/s | - | 15028 | - | 0.40 Pa/m | 6.070 Pa | 66.922 Pa
| Fittings | 6349.6 CMH | - | 4.9 m/s | 14.434 Pa | - | 4.216 | - | 60.852 Pa
53 | Duct | 250.0 CMH | 250 mmø | 1.4 m/s | - | 1672 | - | 0.13 Pa/m | 0.212 Pa | 4.844 Pa
| Fittings | 250.0 CMH | - | 1.4 m/s | 1.203 Pa | - | 3.8495 | - | 4.633 Pa
| Air Terminal | 250.0 CMH | - | - | - | - | - | - | 0.000 Pa
54 | Duct | 500.0 CMH | 250 mmø | 2.8 m/s | - | 5402 | - | 0.44 Pa/m | 2.361 Pa | 187.959 Pa
| Fittings | 500.0 CMH | - | 2.8 m/s | 4.814 Pa | - | 38.5549 | - | 185.598 Pa
55 | Duct | 600.0 CMH | 250 mmø | 3.4 m/s | - | 3190 | - | 0.61 Pa/m | 1.938 Pa | 4.885 Pa
| Fittings | 600.0 CMH | - | 3.4 m/s | 6.932 Pa | - | 0.4252 | - | 2.947 Pa
56 | Duct | 750.0 CMH | 250 mmø | 4.2 m/s | - | 3187 | - | 0.91 Pa/m | 2.902 Pa | 5.010 Pa
| Fittings | 750.0 CMH | - | 4.2 m/s | 10.831 Pa | - | 0.19461 | - | 2.108 Pa
57 | Duct | 850.0 CMH | 250 mmø | 4.8 m/s | - | 383 | - | 1.14 Pa/m | 0.438 Pa | 0.438 Pa
| Fittings | 850.0 CMH | - | 4.8 m/s | 13.912 Pa | - | 0 | - | 0.000 Pa
58 | Duct | 850.0 CMH | 300 mmx300 mm | 2.6 m/s | - | 2820 | - | 0.30 Pa/m | 0.857 Pa | 0.857 Pa
| Fittings | 850.0 CMH | - | 2.6 m/s | 4.139 Pa | - | 0 | - | 0.000 Pa
59 | Duct | 1000.0 CMH | 300 mmx300 mm | 3.1 m/s | - | 1055 | - | 0.41 Pa/m | 0.429 Pa | 0.429 Pa
| Fittings | 1000.0 CMH | - | 3.1 m/s | 5.728 Pa | - | 0 | - | 0.000 Pa
60 | Duct | 1150.0 CMH | 300 mmx300 mm | 3.5 m/s | - | 1356 | - | 0.52 Pa/m | 0.711 Pa | 1.186 Pa
| Fittings | 1150.0 CMH | - | 3.5 m/s | 7.575 Pa | - | 0.062748 | - | 0.475 Pa
61 | Duct | 1150.0 CMH | 350 mmx200 mm | 4.6 m/s | - | 500 | - | 1.02 Pa/m | 0.508 Pa | 15.553 Pa
| Fittings | 1150.0 CMH | - | 4.6 m/s | 12.523 Pa | - | 1.2014 | - | 15.045 Pa
62 | Duct | 1150.0 CMH | 350 mmx200 mm | 4.6 m/s | - | 1692 | - | 1.02 Pa/m | 1.719 Pa | 8.599 Pa
| Fittings | 1150.0 CMH | - | 4.6 m/s | 12.523 Pa | - | 0.54944 | - | 6.880 Pa
63 | Duct | 1150.0 CMH | 400 mmx400 mm | 2.0 m/s | - | 407 | - | 0.13 Pa/m | 0.053 Pa | 0.053 Pa
| Fittings | 1150.0 CMH | - | 2.0 m/s | 2.397 Pa | - | 0 | - | 0.000 Pa
64 | Duct | 150.0 CMH | 160 mmø | 2.1 m/s | - | 1965 | - | 0.44 Pa/m | 0.858 Pa | 178.478 Pa
| Fittings | 150.0 CMH | - | 2.1 m/s | 2.582 Pa | - | 68.7822 | - | 177.620 Pa
| Air Terminal | 150.0 CMH | - | - | - | - | - | - | 0.000 Pa
65 | Duct | 900.0 CMH | 280 mmø | 4.1 m/s | - | 1140 | - | 0.73 Pa/m | 0.831 Pa | 0.831 Pa
| Fittings | 900.0 CMH | - | 4.1 m/s | 9.912 Pa | - | 0 | - | 0.000 Pa
66 | Duct | 900.0 CMH | 280 mmø | 4.1 m/s | - | 3010 | - | 0.73 Pa/m | 2.194 Pa | 9.709 Pa
| Fittings | 900.0 CMH | - | 4.1 m/s | 9.912 Pa | - | 0.75817 | - | 7.515 Pa
67 | Duct | 900.0 CMH | 400 mmx400 mm | 1.6 m/s | - | 414 | - | 0.08 Pa/m | 0.035 Pa | 0.035 Pa
| Fittings | 900.0 CMH | - | 1.6 m/s | 1.468 Pa | - | 0 | - | 0.000 Pa
68 | Duct | 2200.0 CMH | 400 mmx400 mm | 3.8 m/s | - | 415 | - | 0.42 Pa/m | 0.173 Pa | 0.173 Pa
| Fittings | 2200.0 CMH | - | 3.8 m/s | 8.772 Pa | - | 0 | - | 0.000 Pa
69 | Duct | 2450.0 CMH | 400 mmx400 mm | 4.3 m/s | - | 3274 | - | 0.51 Pa/m | 1.663 Pa | 36.684 Pa
| Fittings | 2450.0 CMH | - | 4.3 m/s | 10.879 Pa | - | 3.2192 | - | 35.021 Pa
70 | Duct | 2450.0 CMH | 450 mmx450 mm | 3.4 m/s | - | 853 | - | 0.29 Pa/m | 0.244 Pa | 8.054 Pa
| Fittings | 2450.0 CMH | - | 3.4 m/s | 6.792 Pa | - | 1.15 | - | 7.810 Pa
71 | Duct | 150.0 CMH | 160 mmø | 2.1 m/s | - | 1547 | - | 0.44 Pa/m | 0.676 Pa | 182.113 Pa
| Fittings | 150.0 CMH | - | 2.1 m/s | 2.582 Pa | - | 70.2606 | - | 181.438 Pa
| Air Terminal | 150.0 CMH | - | - | - | - | - | - | 0.000 Pa
72 | Duct | 750.0 CMH | 280 mmø | 3.4 m/s | - | 946 | - | 0.52 Pa/m | 0.495 Pa | 1.782 Pa
| Fittings | 750.0 CMH | - | 3.4 m/s | 6.883 Pa | - | 0.18687 | - | 1.286 Pa
73 | Duct | 100.0 CMH | 160 mmø | 1.4 m/s | - | 1709 | - | 0.21 Pa/m | 0.362 Pa | 177.281 Pa
| Fittings | 100.0 CMH | - | 1.4 m/s | 1.148 Pa | - | 154.1487 | - | 176.918 Pa
| Air Terminal | 100.0 CMH | - | - | - | - | - | - | 0.000 Pa
74 | Duct | 600.0 CMH | 250 mmø | 3.4 m/s | - | 2592 | - | 0.61 Pa/m | 1.575 Pa | 1.900 Pa
| Fittings | 600.0 CMH | - | 3.4 m/s | 6.932 Pa | - | 0.046923 | - | 0.325 Pa
75 | Duct | 600.0 CMH | 280 mmø | 2.7 m/s | - | 300 | - | 0.35 Pa/m | 0.105 Pa | 1.274 Pa
| Fittings | 600.0 CMH | - | 2.7 m/s | 4.405 Pa | - | 0.26531 | - | 1.169 Pa
76 | Duct | 150.0 CMH | 160 mmø | 2.1 m/s | - | 1711 | - | 0.44 Pa/m | 0.747 Pa | 184.327 Pa
| Fittings | 150.0 CMH | - | 2.1 m/s | 2.582 Pa | - | 71.09 | - | 183.580 Pa
| Air Terminal | 150.0 CMH | - | - | - | - | - | - | 0.000 Pa
77 | Duct | 500.0 CMH | 250 mmø | 2.8 m/s | - | 3187 | - | 0.44 Pa/m | 1.393 Pa | 2.991 Pa
| Fittings | 500.0 CMH | - | 2.8 m/s | 4.814 Pa | - | 0.33187 | - | 1.598 Pa
78 | Duct | 100.0 CMH | 160 mmø | 1.4 m/s | - | 1711 | - | 0.21 Pa/m | 0.363 Pa | 182.609 Pa
| Fittings | 100.0 CMH | - | 1.4 m/s | 1.148 Pa | - | 158.7911 | - | 182.246 Pa
| Air Terminal | 100.0 CMH | - | - | - | - | - | - | 0.000 Pa
79 | Duct | 350.0 CMH | 250 mmø | 2.0 m/s | - | 3190 | - | 0.23 Pa/m | 0.736 Pa | 2.677 Pa
| Fittings | 350.0 CMH | - | 2.0 m/s | 2.359 Pa | - | 0.82328 | - | 1.942 Pa
80 | Duct | 266.6 CMH | 250 mmø | 1.5 m/s | - | 8348 | - | 0.14 Pa/m | 1.185 Pa | 4.612 Pa
| Fittings | 266.6 CMH | - | 1.5 m/s | 1.369 Pa | - | 2.5045 | - | 3.428 Pa
| Air Terminal | 266.6 CMH | - | - | - | - | - | - | 0.000 Pa
81 | Duct | 533.2 CMH | 250 mmø | 3.0 m/s | - | 3530 | - | 0.49 Pa/m | 1.733 Pa | 5.200 Pa
| Fittings | 533.2 CMH | - | 3.0 m/s | 5.474 Pa | - | 0.63333 | - | 3.467 Pa
82 | Duct | 799.8 CMH | 250 mmø | 4.5 m/s | - | 562 | - | 1.02 Pa/m | 0.576 Pa | 2.761 Pa
| Fittings | 799.8 CMH | - | 4.5 m/s | 12.317 Pa | - | 0.17745 | - | 2.186 Pa
83 | Fittings | 799.8 CMH | - | 0.0 m/s | 30.072 Pa | - | 6.1929 | - | 186.229 Pa | 186.229 Pa
84 | Duct | 799.8 CMH | 250 mmø | 4.5 m/s | - | 1896 | - | 1.02 Pa/m | 1.940 Pa | 5.940 Pa
| Fittings | 799.8 CMH | - | 4.5 m/s | 12.317 Pa | - | 0.32475 | - | 4.000 Pa
85 | Duct | 799.8 CMH | 300 mmx300 mm | 2.5 m/s | - | 278 | - | 0.27 Pa/m | 0.076 Pa | 0.076 Pa
| Fittings | 799.8 CMH | - | 2.5 m/s | 3.664 Pa | - | 0 | - | 0.000 Pa
86 | Duct | 1449.8 CMH | 300 mmx300 mm | 4.5 m/s | - | 9938 | - | 0.80 Pa/m | 7.932 Pa | 7.932 Pa
| Fittings | 1449.8 CMH | - | 4.5 m/s | 12.040 Pa | - | 0 | - | 0.000 Pa
87 | Duct | 1449.8 CMH | 300 mmx300 mm | 4.5 m/s | - | 3811 | - | 0.80 Pa/m | 3.042 Pa | 44.447 Pa
| Fittings | 1449.8 CMH | - | 4.5 m/s | 12.040 Pa | - | 3.439 | - | 41.405 Pa
88 | Duct | 1449.8 CMH | 400 mmx400 mm | 2.5 m/s | - | 155 | - | 0.20 Pa/m | 0.030 Pa | 0.030 Pa
| Fittings | 1449.8 CMH | - | 2.5 m/s | 3.810 Pa | - | 0 | - | 0.000 Pa
89 | Duct | 1749.8 CMH | 400 mmx400 mm | 3.0 m/s | - | 643 | - | 0.28 Pa/m | 0.178 Pa | 0.178 Pa
| Fittings | 1749.8 CMH | - | 3.0 m/s | 5.549 Pa | - | 0 | - | 0.000 Pa
90 | Duct | 2249.8 CMH | 400 mmx400 mm | 3.9 m/s | - | 399 | - | 0.44 Pa/m | 0.174 Pa | 0.174 Pa
| Fittings | 2249.8 CMH | - | 3.9 m/s | 9.174 Pa | - | 0 | - | 0.000 Pa
91 | Duct | 2249.8 CMH | 400 mmx400 mm | 3.9 m/s | - | 1191 | - | 0.44 Pa/m | 0.518 Pa | 0.518 Pa
| Fittings | 2249.8 CMH | - | 3.9 m/s | 9.174 Pa | - | 0 | - | 0.000 Pa
92 | Duct | 100.0 CMH | 160 mmø | 1.4 m/s | - | 1454 | - | 0.21 Pa/m | 0.308 Pa | 181.108 Pa
| Fittings | 100.0 CMH | - | 1.4 m/s | 1.148 Pa | - | 157.5308 | - | 180.800 Pa
| Air Terminal | 100.0 CMH | - | - | - | - | - | - | 0.000 Pa
93 | Duct | 350.0 CMH | 200 mmx200 mm | 2.4 m/s | - | 3450 | - | 0.44 Pa/m | 1.517 Pa | 1.517 Pa
| Fittings | 350.0 CMH | - | 2.4 m/s | 3.552 Pa | - | 0 | - | 0.000 Pa
94 | Duct | 450.0 CMH | 200 mmx200 mm | 3.1 m/s | - | 3450 | - | 0.69 Pa/m | 2.384 Pa | 2.384 Pa
| Fittings | 450.0 CMH | - | 3.1 m/s | 5.872 Pa | - | 0 | - | 0.000 Pa
95 | Duct | 550.0 CMH | 200 mmx200 mm | 3.8 m/s | - | 3450 | - | 0.99 Pa/m | 3.428 Pa | 3.428 Pa
| Fittings | 550.0 CMH | - | 3.8 m/s | 8.772 Pa | - | 0 | - | 0.000 Pa
96 | Duct | 650.0 CMH | 200 mmx200 mm | 4.5 m/s | - | 849 | - | 1.35 Pa/m | 1.143 Pa | 1.143 Pa
| Fittings | 650.0 CMH | - | 4.5 m/s | 12.252 Pa | - | 0 | - | 0.000 Pa
97 | Duct | 650.0 CMH | 200 mmx200 mm | 4.5 m/s | - | 434 | - | 1.35 Pa/m | 0.584 Pa | 32.870 Pa
| Fittings | 650.0 CMH | - | 4.5 m/s | 12.252 Pa | - | 2.6352 | - | 32.286 Pa
98 | Fittings | 650.0 CMH | - | 0.0 m/s | 5.018 Pa | - | 5.9781 | - | 30.000 Pa | 30.000 Pa
99 | Duct | 650.0 CMH | 200 mmx200 mm | 4.5 m/s | - | 1586 | - | 1.35 Pa/m | 2.135 Pa | 180.314 Pa
| Fittings | 650.0 CMH | - | 4.5 m/s | 12.252 Pa | - | 14.5431 | - | 178.179 Pa
100 | Duct | 650.0 CMH | 200 mmx200 mm | 4.5 m/s | - | 22 | - | 1.35 Pa/m | 0.030 Pa | 0.030 Pa
| Fittings | 650.0 CMH | - | 4.5 m/s | 12.252 Pa | - | 0 | - | 0.000 Pa
101 | Duct | 266.6 CMH | 250 mmø | 1.5 m/s | - | 346 | - | 0.14 Pa/m | 0.049 Pa | 3.948 Pa
| Fittings | 266.6 CMH | - | 1.5 m/s | 1.369 Pa | - | 2.8491 | - | 3.899 Pa
| Air Terminal | 266.6 CMH | - | - | - | - | - | - | 0.000 Pa
102 | Duct | 533.2 CMH | 250 mmø | 3.0 m/s | - | 5832 | - | 0.49 Pa/m | 2.863 Pa | 7.930 Pa
| Fittings | 533.2 CMH | - | 3.0 m/s | 5.474 Pa | - | 0.92561 | - | 5.067 Pa
103 | Duct | 799.8 CMH | 250 mmø | 4.5 m/s | - | 687 | - | 1.02 Pa/m | 0.703 Pa | 2.889 Pa
| Fittings | 799.8 CMH | - | 4.5 m/s | 12.317 Pa | - | 0.17745 | - | 2.186 Pa
104 | Duct | 799.8 CMH | 200 mmø | 7.1 m/s | - | 194 | - | 3.07 Pa/m | 0.595 Pa | 191.290 Pa
| Fittings | 799.8 CMH | - | 7.1 m/s | 30.072 Pa | - | 6.3414 | - | 190.695 Pa
105 | Fittings | 799.8 CMH | - | 0.0 m/s | 3.664 Pa | - | 0 | - | 0.000 Pa | 0.000 Pa
106 | Duct | 799.8 CMH | 300 mmx300 mm | 2.5 m/s | - | 117 | - | 0.27 Pa/m | 0.032 Pa | 4.245 Pa
| Fittings | 799.8 CMH | - | 2.5 m/s | 3.664 Pa | - | 1.15 | - | 4.214 Pa
107 | Duct | 1449.8 CMH | 300 mmx300 mm | 4.5 m/s | - | 15799 | - | 0.80 Pa/m | 12.609 Pa | 53.933 Pa
| Fittings | 1449.8 CMH | - | 4.5 m/s | 12.040 Pa | - | 3.4322 | - | 41.323 Pa
108 | Duct | 1449.8 CMH | 400 mmx400 mm | 3.5 m/s | - | 1500 | - | 0.35 Pa/m | 0.527 Pa | 0.527 Pa
| Fittings | 1449.8 CMH | - | 3.5 m/s | 7.248 Pa | - | 0 | - | 0.000 Pa
109 | Duct | 1999.8 CMH | 400 mmx400 mm | 3.5 m/s | - | 2691 | - | 0.35 Pa/m | 0.419 Pa | 0.946 Pa
| Fittings | 1999.8 CMH | - | 3.5 m/s | 7.248 Pa | - | 0 | - | 0.000 Pa
110 | Duct | 2249.8 CMH | 400 mmx400 mm | 3.9 m/s | - | 6145 | - | 0.44 Pa/m | 2.673 Pa | 13.365 Pa
| Fittings | 2249.8 CMH | - | 3.9 m/s | 9.174 Pa | - | 1.1654 | - | 10.691 Pa
111 | Fittings | 2249.8 CMH | - | 0.0 m/s | 14.434 Pa | - | 0 | - | 0.000 Pa | 0.000 Pa
112 | Duct | 200.0 CMH | 160 mmø | 2.8 m/s | - | 4667 | - | 0.73 Pa/m | 3.416 Pa | 6.180 Pa
| Fittings | 200.0 CMH | - | 2.8 m/s | 4.591 Pa | - | 0.60203 | - | 2.764 Pa
| Air Terminal | 200.0 CMH | - | - | - | - | - | - | 0.000 Pa
113 | Fittings | 200.0 CMH | - | 0.0 m/s | 2.866 Pa | - | 2.0359 | - | 5.835 Pa | 5.835 Pa
114 | Duct | 150.0 CMH | 160 mmø | 2.1 m/s | - | 1703 | - | 0.44 Pa/m | 0.744 Pa | 180.649 Pa
| Fittings | 150.0 CMH | - | 2.1 m/s | 2.582 Pa | - | 69.6671 | - | 179.905 Pa
| Air Terminal | 150.0 CMH | - | - | - | - | - | - | 0.000 Pa
115 | Duct | 250.0 CMH | 250 mmø | 1.4 m/s | - | 1672 | - | 0.13 Pa/m | 0.212 Pa | 4.844 Pa
| Fittings | 250.0 CMH | - | 1.4 m/s | 1.203 Pa | - | 3.8495 | - | 4.633 Pa
| Air Terminal | 250.0 CMH | - | - | - | - | - | - | 0.000 Pa
116 | Duct | 266.6 CMH | 250 mmø | 1.5 m/s | - | 519 | - | 0.14 Pa/m | 0.074 Pa | 0.737 Pa
| Fittings | 266.6 CMH | - | 1.5 m/s | 1.369 Pa | - | 0.48454 | - | 0.663 Pa
| Air Terminal | 266.6 CMH | - | - | - | - | - | - | 0.000 Pa
117 | Duct | 266.6 CMH | 250 mmø | 1.5 m/s | - | 6131 | - | 0.14 Pa/m | 0.870 Pa | 5.898 Pa
| Fittings | 266.6 CMH | - | 1.5 m/s | 1.369 Pa | - | 3.6736 | - | 5.028 Pa
| Air Terminal | 266.6 CMH | - | - | - | - | - | - | 0.000 Pa
118 | Duct | 150.0 CMH | 160 mmø | 2.1 m/s | - | 3600 | - | 0.44 Pa/m | 1.572 Pa | 8.930 Pa
| Fittings | 150.0 CMH | - | 2.1 m/s | 2.582 Pa | - | 2.8494 | - | 7.358 Pa
| Air Terminal | 150.0 CMH | - | - | - | - | - | - | 0.000 Pa
119 | Duct | 300.0 CMH | 160 mmø | 4.1 m/s | - | 3640 | - | 1.52 Pa/m | 5.545 Pa | 188.929 Pa
| Fittings | 300.0 CMH | - | 4.1 m/s | 10.329 Pa | - | 17.7536 | - | 183.384 Pa
120 | Duct | 300.0 CMH | 200 mmø | 2.7 m/s | - | 7608 | - | 0.51 Pa/m | 3.914 Pa | 4.966 Pa
| Fittings | 300.0 CMH | - | 2.7 m/s | 4.231 Pa | - | 0.24864 | - | 1.052 Pa
121 | Duct | 300.0 CMH | 300 mmx200 mm | 1.4 m/s | - | 1291 | - | 0.13 Pa/m | 0.166 Pa | -0.634 Pa
| Fittings | 300.0 CMH | - | 1.4 m/s | 1.160 Pa | - | -0.69 | - | -0.800 Pa
122 | Duct | 800.0 CMH | 300 mmx200 mm | 3.7 m/s | - | 575 | - | 0.75 Pa/m | 0.430 Pa | 2.656 Pa
| Fittings | 800.0 CMH | - | 3.7 m/s | 8.248 Pa | - | 0.26985 | - | 2.226 Pa
123 | Fittings | 800.0 CMH | - | 0.0 m/s | 6.060 Pa | - | 0 | - | 0.000 Pa | 0.000 Pa
124 | Duct | 800.0 CMH | 350 mmx200 mm | 3.2 m/s | - | 335 | - | 0.53 Pa/m | 0.176 Pa | 0.176 Pa
| Fittings | 800.0 CMH | - | 3.2 m/s | 6.060 Pa | - | 0 | - | 0.000 Pa
125 | Duct | 1100.0 CMH | 350 mmx200 mm | 4.4 m/s | - | 10000 | - | 0.94 Pa/m | 9.368 Pa | 9.368 Pa
| Fittings | 1100.0 CMH | - | 4.4 m/s | 11.457 Pa | - | 0 | - | 0.000 Pa
126 | Duct | 1100.0 CMH | 350 mmx200 mm | 4.4 m/s | - | 1733 | - | 0.94 Pa/m | 1.624 Pa | 1.624 Pa
| Fittings | 1100.0 CMH | - | 4.4 m/s | 11.457 Pa | - | 0 | - | 0.000 Pa
127 | Fittings | 1100.0 CMH | - | 0.0 m/s | 11.457 Pa | - | 1.2014 | - | 13.765 Pa | 13.765 Pa
128 | Duct | 1100.0 CMH | 350 mmx200 mm | 4.4 m/s | - | 2632 | - | 0.94 Pa/m | 2.466 Pa | 2.466 Pa
| Fittings | 1100.0 CMH | - | 4.4 m/s | 11.457 Pa | - | 0 | - | 0.000 Pa
129 | Duct | 1100.0 CMH | 350 mmx250 mm | 3.5 m/s | - | 374 | - | 0.53 Pa/m | 0.197 Pa | 8.881 Pa
| Fittings | 1100.0 CMH | - | 3.5 m/s | 7.333 Pa | - | 1.1843 | - | 8.684 Pa
130 | Duct | 1100.0 CMH | 400 mmx300 mm | 2.5 m/s | - | 493 | - | 0.24 Pa/m | 0.120 Pa | 0.120 Pa
| Fittings | 1100.0 CMH | - | 2.5 m/s | 3.899 Pa | - | 0 | - | 0.000 Pa
131 | Duct | 1600.0 CMH | 400 mmx300 mm | 3.7 m/s | - | 4017 | - | 0.48 Pa/m | 1.924 Pa | 26.365 Pa
| Fittings | 1600.0 CMH | - | 3.7 m/s | 8.248 Pa | - | 2.9631 | - | 24.441 Pa
132 | Duct | 1600.0 CMH | 350 mmx350 mm | 3.6 m/s | - | 1301 | - | 0.45 Pa/m | 0.585 Pa | 0.585 Pa
| Fittings | 1600.0 CMH | - | 3.6 m/s | 7.915 Pa | - | 0 | - | 0.000 Pa
133 | Duct | 1600.0 CMH | 350 mmx350 mm | 3.6 m/s | - | 1565 | - | 0.45 Pa/m | 0.704 Pa | 12.141 Pa
| Fittings | 1600.0 CMH | - | 3.6 m/s | 7.915 Pa | - | 1.4449 | - | 11.437 Pa
134 | Duct | 1600.0 CMH | 500 mmx500 mm | 1.8 m/s | - | 1880 | - | 0.08 Pa/m | 0.150 Pa | 0.150 Pa
| Fittings | 1600.0 CMH | - | 1.8 m/s | 1.900 Pa | - | 0 | - | 0.000 Pa
135 | Duct | 150.0 CMH | 160 mmø | 2.1 m/s | - | 3125 | - | 0.44 Pa/m | 1.365 Pa | 186.347 Pa
| Fittings | 150.0 CMH | - | 2.1 m/s | 2.582 Pa | - | 71.6333 | - | 184.982 Pa
| Air Terminal | 150.0 CMH | - | - | - | - | - | - | 0.000 Pa
136 | Duct | 250.0 CMH | 160 mmø | 3.5 m/s | - | 1092 | - | 1.09 Pa/m | 1.195 Pa | 3.184 Pa
| Fittings | 250.0 CMH | - | 3.5 m/s | 7.173 Pa | - | 0.2773 | - | 1.989 Pa
137 | Duct | 250.0 CMH | 200 mmx200 mm | 1.7 m/s | - | 385 | - | 0.24 Pa/m | 0.093 Pa | 0.093 Pa
| Fittings | 250.0 CMH | - | 1.7 m/s | 1.812 Pa | - | 0 | - | 0.000 Pa
138 | Duct | 100.0 CMH | 160 mmø | 1.4 m/s | - | 1451 | - | 0.21 Pa/m | 0.307 Pa | 181.107 Pa
| Fittings | 100.0 CMH | - | 1.4 m/s | 1.148 Pa | - | 157.5308 | - | 180.800 Pa
| Air Terminal | 100.0 CMH | - | - | - | - | - | - | 0.000 Pa
139 | Duct | 300.0 CMH | 200 mmx200 mm | 2.1 m/s | - | 3450 | - | 0.33 Pa/m | 1.151 Pa | 1.151 Pa
| Fittings | 300.0 CMH | - | 2.1 m/s | 2.610 Pa | - | 0 | - | 0.000 Pa
140 | Duct | 400.0 CMH | 200 mmx200 mm | 2.8 m/s | - | 3450 | - | 0.56 Pa/m | 1.928 Pa | 1.928 Pa
| Fittings | 400.0 CMH | - | 2.8 m/s | 4.640 Pa | - | 0 | - | 0.000 Pa
141 | Duct | 500.0 CMH | 200 mmx200 mm | 3.5 m/s | - | 1058 | - | 0.84 Pa/m | 0.885 Pa | 0.885 Pa
| Fittings | 500.0 CMH | - | 3.5 m/s | 7.250 Pa | - | 0 | - | 0.000 Pa
142 | Duct | 500.0 CMH | 200 mmx200 mm | 3.5 m/s | - | 304 | - | 0.84 Pa/m | 0.255 Pa | 9.647 Pa
| Fittings | 500.0 CMH | - | 3.5 m/s | 7.250 Pa | - | 1.2956 | - | 9.392 Pa
143 | Fittings | 500.0 CMH | - | 0.0 m/s | 2.969 Pa | - | 10.2566 | - | 30.456 Pa | 30.456 Pa
144 | Fittings | 500.0 CMH | - | 0.0 m/s | 7.250 Pa | - | 20.7904 | - | 150.721 Pa | 150.721 Pa
145 | Duct | 500.0 CMH | 200 mmx200 mm | 3.5 m/s | - | 69 | - | 0.84 Pa/m | 0.058 Pa | 5.576 Pa
| Fittings | 500.0 CMH | - | 3.5 m/s | 7.250 Pa | - | 0.76109 | - | 5.518 Pa
146 | Duct | 100.0 CMH | 160 mmø | 1.4 m/s | - | 1452 | - | 0.21 Pa/m | 0.308 Pa | 181.108 Pa
| Fittings | 100.0 CMH | - | 1.4 m/s | 1.148 Pa | - | 157.5308 | - | 180.800 Pa
| Air Terminal | 100.0 CMH | - | - | - | - | - | - | 0.000 Pa
147 | Duct | 200.0 CMH | 200 mmx200 mm | 1.4 m/s | - | 3450 | - | 0.16 Pa/m | 0.559 Pa | 0.559 Pa
| Fittings | 200.0 CMH | - | 1.4 m/s | 1.160 Pa | - | 0 | - | 0.000 Pa
148 | Duct | 100.0 CMH | 160 mmø | 1.4 m/s | - | 1557 | - | 0.21 Pa/m | 0.330 Pa | 182.118 Pa
| Fittings | 100.0 CMH | - | 1.4 m/s | 1.148 Pa | - | 158.392 | - | 181.788 Pa
| Air Terminal | 100.0 CMH | - | - | - | - | - | - | 0.000 Pa
149 | Duct | 100.0 CMH | 200 mmx200 mm | 0.7 m/s | - | 382 | - | 0.05 Pa/m | 0.018 Pa | 0.018 Pa
| Fittings | 100.0 CMH | - | 0.7 m/s | 0.290 Pa | - | 0 | - | 0.000 Pa
150 | Duct | 300.0 CMH | - | 2.7 m/s | - | 493 | - | 0.51 Pa/m | 0.253 Pa | 7.004 Pa
| Fittings | 300.0 CMH | - | 2.7 m/s | 4.231 Pa | - | 1.5956 | - | 6.751 Pa
| Air Terminal | 300.0 CMH | - | - | - | - | - | - | 0.000 Pa
151 | Duct | 600.0 CMH | 250 mmø | 3.4 m/s | - | 1693 | - | 0.61 Pa/m | 1.028 Pa | 192.976 Pa
| Fittings | 600.0 CMH | - | 3.4 m/s | 6.932 Pa | - | 27.6902 | - | 191.947 Pa
152 | Duct | 950.0 CMH | 280 mmø | 4.3 m/s | - | 671 | - | 0.80 Pa/m | 0.539 Pa | 4.392 Pa
| Fittings | 950.0 CMH | - | 4.3 m/s | 11.044 Pa | - | 0.3488 | - | 3.852 Pa
153 | Duct | 1150.0 CMH | 280 mmø | 5.2 m/s | - | 6538 | - | 1.14 Pa/m | 7.451 Pa | 9.322 Pa
| Fittings | 1150.0 CMH | - | 5.2 m/s | 16.184 Pa | - | 0.11563 | - | 1.871 Pa
154 | Duct | 1300.0 CMH | 280 mmø | 5.9 m/s | - | 14534 | - | 1.43 Pa/m | 20.735 Pa | 22.335 Pa
| Fittings | 1300.0 CMH | - | 5.9 m/s | 20.681 Pa | - | 0.077366 | - | 1.600 Pa
155 | Duct | 300.0 CMH | - | 2.7 m/s | - | 487 | - | 0.51 Pa/m | 0.251 Pa | 7.001 Pa
| Fittings | 300.0 CMH | - | 2.7 m/s | 4.231 Pa | - | 1.5956 | - | 6.751 Pa
| Air Terminal | 300.0 CMH | - | - | - | - | - | - | 0.000 Pa
156 | Duct | 250.0 CMH | 250 mmø | 1.4 m/s | - | 2555 | - | 0.13 Pa/m | 0.323 Pa | 3.434 Pa
| Fittings | 250.0 CMH | - | 1.4 m/s | 1.203 Pa | - | 2.5847 | - | 3.111 Pa
| Air Terminal | 250.0 CMH | - | - | - | - | - | - | 0.000 Pa
157 | Duct | 500.0 CMH | 250 mmø | 2.8 m/s | - | 8653 | - | 0.44 Pa/m | 3.783 Pa | 187.783 Pa
| Fittings | 500.0 CMH | - | 2.8 m/s | 4.814 Pa | - | 38.223 | - | 184.000 Pa
158 | Fittings | 250.0 CMH | - | 0.0 m/s | 1.203 Pa | - | 1.68 | - | 2.022 Pa | 2.022 Pa
| Air Terminal | 250.0 CMH | - | - | - | - | - | - | 0.000 Pa
159 | Duct | 125.0 CMH | 160 mmø | 1.7 m/s | - | 3529 | - | 0.32 Pa/m | 1.113 Pa | 5.356 Pa
| Fittings | 125.0 CMH | - | 1.7 m/s | 1.793 Pa | - | 2.3661 | - | 4.243 Pa
| Air Terminal | 125.0 CMH | - | - | - | - | - | - | 0.000 Pa
160 | Duct | 250.0 CMH | 160 mmø | 3.5 m/s | - | 4259 | - | 1.09 Pa/m | 4.662 Pa | 188.995 Pa
| Fittings | 250.0 CMH | - | 3.5 m/s | 7.173 Pa | - | 25.6975 | - | 184.333 Pa
161 | Duct | 250.0 CMH | 250 mmø | 1.4 m/s | - | 135 | - | 0.13 Pa/m | 0.017 Pa | 0.939 Pa
| Fittings | 250.0 CMH | - | 1.4 m/s | 1.203 Pa | - | 0.76641 | - | 0.922 Pa
162 | Duct | 125.0 CMH | - | 1.7 m/s | - | 401 | - | 0.32 Pa/m | 0.127 Pa | 3.139 Pa
| Fittings | 125.0 CMH | - | 1.7 m/s | 1.793 Pa | - | 1.68 | - | 3.013 Pa
| Air Terminal | 125.0 CMH | - | - | - | - | - | - | 0.000 Pa
163 | Duct | 100.0 CMH | 160 mmø | 1.4 m/s | - | 1695 | - | 0.21 Pa/m | 0.359 Pa | 171.501 Pa
| Fittings | 100.0 CMH | - | 1.4 m/s | 1.148 Pa | - | 149.1154 | - | 171.142 Pa
| Air Terminal | 100.0 CMH | - | - | - | - | - | - | 0.000 Pa
164 | Duct | 150.0 CMH | 160 mmø | 2.1 m/s | - | 1512 | - | 0.44 Pa/m | 0.661 Pa | 183.061 Pa
| Fittings | 150.0 CMH | - | 2.1 m/s | 2.582 Pa | - | 70.6333 | - | 182.400 Pa
| Air Terminal | 150.0 CMH | - | - | - | - | - | - | 0.000 Pa
165 | Duct | 150.0 CMH | 160 mmø | 2.1 m/s | - | 1182 | - | 0.44 Pa/m | 0.516 Pa | 184.516 Pa
| Fittings | 150.0 CMH | - | 2.1 m/s | 2.582 Pa | - | 71.2528 | - | 184.000 Pa
| Air Terminal | 150.0 CMH | - | - | - | - | - | - | 0.000 Pa
166 | Duct | 100.0 CMH | 160 mmø | 1.4 m/s | - | 1698 | - | 0.21 Pa/m | 0.360 Pa | 177.278 Pa
| Fittings | 100.0 CMH | - | 1.4 m/s | 1.148 Pa | - | 154.1487 | - | 176.918 Pa
| Air Terminal | 100.0 CMH | - | - | - | - | - | - | 0.000 Pa
167 | Duct | 125.0 CMH | 160 mmø | 1.7 m/s | - | 1775 | - | 0.32 Pa/m | 0.560 Pa | 7.203 Pa
| Fittings | 125.0 CMH | - | 1.7 m/s | 1.793 Pa | - | 3.7044 | - | 6.643 Pa
| Air Terminal | 125.0 CMH | - | - | - | - | - | - | 0.000 Pa
168 | Duct | 250.0 CMH | 160 mmø | 3.5 m/s | - | 414 | - | 1.09 Pa/m | 0.454 Pa | 185.349 Pa
| Fittings | 250.0 CMH | - | 3.5 m/s | 7.173 Pa | - | 25.7758 | - | 184.895 Pa
169 | Duct | 250.0 CMH | 280 mmø | 1.1 m/s | - | 282 | - | 0.07 Pa/m | 0.021 Pa | 8.473 Pa
| Fittings | 250.0 CMH | - | 1.1 m/s | 0.765 Pa | - | 11.0507 | - | 8.452 Pa
170 | Duct | 150.0 CMH | 160 mmø | 2.1 m/s | - | 3068 | - | 0.44 Pa/m | 1.340 Pa | 186.322 Pa
| Fittings | 150.0 CMH | - | 2.1 m/s | 2.582 Pa | - | 71.6333 | - | 184.982 Pa
| Air Terminal | 150.0 CMH | - | - | - | - | - | - | 0.000 Pa
171 | Duct | 250.0 CMH | 160 mmø | 3.5 m/s | - | 1092 | - | 1.09 Pa/m | 1.195 Pa | 3.187 Pa
| Fittings | 250.0 CMH | - | 3.5 m/s | 7.173 Pa | - | 0.27769 | - | 1.992 Pa
172 | Duct | 250.0 CMH | 200 mmx200 mm | 1.7 m/s | - | 385 | - | 0.24 Pa/m | 0.093 Pa | 0.093 Pa
| Fittings | 250.0 CMH | - | 1.7 m/s | 1.812 Pa | - | 0 | - | 0.000 Pa
173 | Duct | 350.0 CMH | 200 mmx200 mm | 2.4 m/s | - | 3450 | - | 0.44 Pa/m | 1.517 Pa | 1.517 Pa
| Fittings | 350.0 CMH | - | 2.4 m/s | 3.552 Pa | - | 0 | - | 0.000 Pa
174 | Duct | 450.0 CMH | 200 mmx200 mm | 3.1 m/s | - | 3450 | - | 0.69 Pa/m | 2.384 Pa | 2.384 Pa
| Fittings | 450.0 CMH | - | 3.1 m/s | 5.872 Pa | - | 0 | - | 0.000 Pa
175 | Duct | 550.0 CMH | 200 mmx200 mm | 3.8 m/s | - | 3450 | - | 0.99 Pa/m | 3.428 Pa | 3.428 Pa
| Fittings | 550.0 CMH | - | 3.8 m/s | 8.772 Pa | - | 0 | - | 0.000 Pa
176 | Duct | 650.0 CMH | 200 mmx200 mm | 4.5 m/s | - | 2023 | - | 1.35 Pa/m | 2.723 Pa | 18.496 Pa
| Fittings | 650.0 CMH | - | 4.5 m/s | 12.252 Pa | - | 1.2874 | - | 15.773 Pa
177 | Fittings | 650.0 CMH | - | 0.0 m/s | 5.018 Pa | - | 5.9781 | - | 30.000 Pa | 30.000 Pa
178 | Duct | 650.0 CMH | 200 mmx200 mm | 4.5 m/s | - | 343 | - | 1.35 Pa/m | 0.462 Pa | 150.462 Pa
| Fittings | 650.0 CMH | - | 4.5 m/s | 12.252 Pa | - | 12.2431 | - | 150.000 Pa
179 | Duct | 650.0 CMH | 200 mmx200 mm | 4.5 m/s | - | 643 | - | 1.35 Pa/m | 0.865 Pa | 0.865 Pa
| Fittings | 650.0 CMH | - | 4.5 m/s | 12.252 Pa | - | 0 | - | 0.000 Pa
180 | Duct | 100.0 CMH | 160 mmø | 1.4 m/s | - | 1356 | - | 0.21 Pa/m | 0.287 Pa | 184.911 Pa
| Fittings | 100.0 CMH | - | 1.4 m/s | 1.148 Pa | - | 160.8619 | - | 184.623 Pa
| Air Terminal | 100.0 CMH | - | - | - | - | - | - | 0.000 Pa
181 | Duct | 150.0 CMH | 160 mmø | 2.1 m/s | - | 3143 | - | 0.44 Pa/m | 1.373 Pa | 180.388 Pa
| Fittings | 150.0 CMH | - | 2.1 m/s | 2.582 Pa | - | 69.3225 | - | 179.015 Pa
| Air Terminal | 150.0 CMH | - | - | - | - | - | - | 0.000 Pa
182 | Fittings | 250.0 CMH | - | 0.0 m/s | 2.938 Pa | - | 0.1125 | - | 0.331 Pa | 0.331 Pa
| Air Terminal | 250.0 CMH | - | - | - | - | - | - | 0.000 Pa
183 | Duct | 250.0 CMH | 160 mmø | 3.5 m/s | - | 758 | - | 1.09 Pa/m | 0.830 Pa | 182.430 Pa
| Fittings | 250.0 CMH | - | 3.5 m/s | 7.173 Pa | - | 25.3164 | - | 181.600 Pa
184 | Duct | 300.0 CMH | 250 mmø | 1.7 m/s | - | 4009 | - | 0.18 Pa/m | 0.702 Pa | 186.401 Pa
| Fittings | 300.0 CMH | - | 1.7 m/s | 1.733 Pa | - | 107.1555 | - | 185.699 Pa
| Air Terminal | 300.0 CMH | - | - | - | - | - | - | 0.000 Pa
185 | Duct | 250.0 CMH | 250 mmø | 1.4 m/s | - | 8516 | - | 0.13 Pa/m | 1.078 Pa | 186.678 Pa
| Fittings | 250.0 CMH | - | 1.4 m/s | 1.203 Pa | - | 154.2215 | - | 185.600 Pa
| Air Terminal | 250.0 CMH | - | - | - | - | - | - | 0.000 Pa
186 | Fittings | 266.6 CMH | - | 0.0 m/s | 1.369 Pa | - | -0.1 | - | -0.137 Pa | -0.137 Pa
| Air Terminal | 266.6 CMH | - | - | - | - | - | - | 0.000 Pa
187 | Fittings | 266.6 CMH | - | 0.0 m/s | 1.369 Pa | - | 1.68 | - | 2.299 Pa | 2.299 Pa
| Air Terminal | 266.6 CMH | - | - | - | - | - | - | 0.000 Pa
188 | Duct | 175.0 CMH | 160 mmø | 2.4 m/s | - | 4873 | - | 0.58 Pa/m | 2.805 Pa | 11.954 Pa
| Fittings | 175.0 CMH | - | 2.4 m/s | 3.515 Pa | - | 2.6028 | - | 9.149 Pa
| Air Terminal | 175.0 CMH | - | - | - | - | - | - | 0.000 Pa
189 | Duct | 350.0 CMH | 160 mmø | 4.8 m/s | - | 14097 | - | 2.02 Pa/m | 28.434 Pa | 220.178 Pa
| Fittings | 350.0 CMH | - | 4.8 m/s | 14.059 Pa | - | 13.638 | - | 191.744 Pa
190 | Fittings | 350.0 CMH | - | 0.0 m/s | 1.499 Pa | - | 6.5406 | - | 9.805 Pa | 9.805 Pa
191 | Duct | 175.0 CMH | 160 mmø | 2.4 m/s | - | 723 | - | 0.58 Pa/m | 0.416 Pa | 7.921 Pa
| Fittings | 175.0 CMH | - | 2.4 m/s | 3.515 Pa | - | 2.1352 | - | 7.505 Pa
| Air Terminal | 175.0 CMH | - | - | - | - | - | - | 0.000 Pa
192 | Duct | 400.0 CMH | 250 mmø | 2.3 m/s | - | 2442 | - | 0.29 Pa/m | 0.715 Pa | 188.291 Pa
| Fittings | 400.0 CMH | - | 2.3 m/s | 3.081 Pa | - | 60.8841 | - | 187.576 Pa
| Air Terminal | 400.0 CMH | - | - | - | - | - | - | 0.000 Pa
193 | Duct | 100.0 CMH | 160 mmø | 1.4 m/s | - | 1448 | - | 0.21 Pa/m | 0.307 Pa | 181.107 Pa
| Fittings | 100.0 CMH | - | 1.4 m/s | 1.148 Pa | - | 157.5308 | - | 180.800 Pa
| Air Terminal | 100.0 CMH | - | - | - | - | - | - | 0.000 Pa
194 | Duct | 100.0 CMH | 160 mmø | 1.4 m/s | - | 1448 | - | 0.21 Pa/m | 0.307 Pa | 181.107 Pa
| Fittings | 100.0 CMH | - | 1.4 m/s | 1.148 Pa | - | 157.5308 | - | 180.800 Pa
| Air Terminal | 100.0 CMH | - | - | - | - | - | - | 0.000 Pa
195 | Duct | 100.0 CMH | 160 mmø | 1.4 m/s | - | 1448 | - | 0.21 Pa/m | 0.307 Pa | 181.107 Pa
| Fittings | 100.0 CMH | - | 1.4 m/s | 1.148 Pa | - | 157.5308 | - | 180.800 Pa
| Air Terminal | 100.0 CMH | - | - | - | - | - | - | 0.000 Pa
196 | Duct | 100.0 CMH | 160 mmø | 1.4 m/s | - | 1448 | - | 0.21 Pa/m | 0.307 Pa | 181.107 Pa
| Fittings | 100.0 CMH | - | 1.4 m/s | 1.148 Pa | - | 157.5308 | - | 180.800 Pa
| Air Terminal | 100.0 CMH | - | - | - | - | - | - | 0.000 Pa
197 | Duct | 150.0 CMH | 160 mmø | 2.1 m/s | - | 612 | - | 0.44 Pa/m | 0.267 Pa | 6.206 Pa
| Fittings | 150.0 CMH | - | 2.1 m/s | 2.582 Pa | - | 2.2996 | - | 5.938 Pa
| Air Terminal | 150.0 CMH | - | - | - | - | - | - | 0.000 Pa
198 | Duct | 250.0 CMH | 250 mmø | 1.4 m/s | - | 1088 | - | 0.13 Pa/m | 0.138 Pa | 183.759 Pa
| Fittings | 250.0 CMH | - | 1.4 m/s | 1.203 Pa | - | 152.5778 | - | 183.622 Pa
| Air Terminal | 250.0 CMH | - | - | - | - | - | - | 0.000 Pa
199 | Duct | 500.0 CMH | 250 mmø | 2.8 m/s | - | 210 | - | 0.44 Pa/m | 0.092 Pa | 0.092 Pa
| Fittings | 500.0 CMH | - | 2.8 m/s | 4.814 Pa | - | 0 | - | 0.000 Pa
200 | Duct | 200.0 CMH | 160 mmø | 2.8 m/s | - | 16625 | - | 0.73 Pa/m | 12.166 Pa | 192.966 Pa
| Fittings | 200.0 CMH | - | 2.8 m/s | 4.591 Pa | - | 39.3826 | - | 180.800 Pa
| Air Terminal | 200.0 CMH | - | - | - | - | - | - | 0.000 Pa
201 | Duct | 250.0 CMH | 250 mmø | 1.4 m/s | - | 6860 | - | 0.13 Pa/m | 0.868 Pa | 184.779 Pa
| Fittings | 250.0 CMH | - | 1.4 m/s | 1.203 Pa | - | 152.8178 | - | 183.911 Pa
| Air Terminal | 250.0 CMH | - | - | - | - | - | - | 0.000 Pa
202 | Duct | 125.0 CMH | 160 mmø | 1.7 m/s | - | 421 | - | 0.32 Pa/m | 0.133 Pa | 5.546 Pa
| Fittings | 125.0 CMH | - | 1.7 m/s | 1.793 Pa | - | 3.0183 | - | 5.413 Pa
| Air Terminal | 125.0 CMH | - | - | - | - | - | - | 0.000 Pa
203 | Duct | 350.0 CMH | 200 mmø | 3.1 m/s | - | 980 | - | 0.68 Pa/m | 0.666 Pa | 2.914 Pa
| Fittings | 350.0 CMH | - | 3.1 m/s | 5.759 Pa | - | 0.39034 | - | 2.248 Pa
| Air Terminal | 350.0 CMH | - | - | - | - | - | - | 0.000 Pa
204 | Duct | 350.0 CMH | 160 mmø | 4.8 m/s | - | 1444 | - | 2.02 Pa/m | 2.912 Pa | 183.712 Pa
| Fittings | 350.0 CMH | - | 4.8 m/s | 14.059 Pa | - | 12.8597 | - | 180.800 Pa
205 | Duct | 100.0 CMH | 160 mmø | 1.4 m/s | - | 1450 | - | 0.21 Pa/m | 0.307 Pa | 181.107 Pa
| Fittings | 100.0 CMH | - | 1.4 m/s | 1.148 Pa | - | 157.5308 | - | 180.800 Pa
| Air Terminal | 100.0 CMH | - | - | - | - | - | - | 0.000 Pa
206 | Duct | 150.0 CMH | 160 mmø | 2.1 m/s | - | 2756 | - | 0.44 Pa/m | 1.204 Pa | 175.350 Pa
| Fittings | 150.0 CMH | - | 2.1 m/s | 2.582 Pa | - | 67.437 | - | 174.146 Pa
| Air Terminal | 150.0 CMH | - | - | - | - | - | - | 0.000 Pa
207 | Duct | 300.0 CMH | 250 mmø | 1.7 m/s | - | 250 | - | 0.18 Pa/m | 0.044 Pa | 0.239 Pa
| Fittings | 300.0 CMH | - | 1.7 m/s | 1.733 Pa | - | 0.1125 | - | 0.195 Pa
| Air Terminal | 300.0 CMH | - | - | - | - | - | - | 0.000 Pa
208 | Duct | 300.0 CMH | 200 mmø | 2.7 m/s | - | 909 | - | 0.51 Pa/m | 0.468 Pa | 182.068 Pa
| Fittings | 300.0 CMH | - | 2.7 m/s | 4.231 Pa | - | 42.922 | - | 181.600 Pa
209 | Duct | 250.0 CMH | 200 mmø | 2.2 m/s | - | 994 | - | 0.37 Pa/m | 0.369 Pa | 182.769 Pa
| Fittings | 250.0 CMH | - | 2.2 m/s | 2.938 Pa | - | 62.08 | - | 182.400 Pa
| Air Terminal | 250.0 CMH | - | - | - | - | - | - | 0.000 Pa
210 | Duct | 100.0 CMH | 160 mmø | 1.4 m/s | - | 1451 | - | 0.21 Pa/m | 0.307 Pa | 181.107 Pa
| Fittings | 100.0 CMH | - | 1.4 m/s | 1.148 Pa | - | 157.5308 | - | 180.800 Pa
| Air Terminal | 100.0 CMH | - | - | - | - | - | - | 0.000 Pa
211 | Duct | 100.0 CMH | 160 mmø | 1.4 m/s | - | 1356 | - | 0.21 Pa/m | 0.287 Pa | 184.911 Pa
| Fittings | 100.0 CMH | - | 1.4 m/s | 1.148 Pa | - | 160.8619 | - | 184.623 Pa
| Air Terminal | 100.0 CMH | - | - | - | - | - | - | 0.000 Pa
212 | Duct | 100.0 CMH | 160 mmø | 1.4 m/s | - | 1454 | - | 0.21 Pa/m | 0.308 Pa | 181.108 Pa
| Fittings | 100.0 CMH | - | 1.4 m/s | 1.148 Pa | - | 157.5308 | - | 180.800 Pa
| Air Terminal | 100.0 CMH | - | - | - | - | - | - | 0.000 Pa
213 | Duct | 100.0 CMH | 160 mmø | 1.4 m/s | - | 1461 | - | 0.21 Pa/m | 0.310 Pa | 181.110 Pa
| Fittings | 100.0 CMH | - | 1.4 m/s | 1.148 Pa | - | 157.5308 | - | 180.800 Pa
| Air Terminal | 100.0 CMH | - | - | - | - | - | - | 0.000 Pa
214 | Duct | 100.0 CMH | 160 mmø | 1.4 m/s | - | 1461 | - | 0.21 Pa/m | 0.310 Pa | 181.110 Pa
| Fittings | 100.0 CMH | - | 1.4 m/s | 1.148 Pa | - | 157.5308 | - | 180.800 Pa
| Air Terminal | 100.0 CMH | - | - | - | - | - | - | 0.000 Pa
215 | Duct | 300.0 CMH | 250 mmø | 1.7 m/s | - | 4043 | - | 0.18 Pa/m | 0.708 Pa | 186.308 Pa
| Fittings | 300.0 CMH | - | 1.7 m/s | 1.733 Pa | - | 107.0983 | - | 185.600 Pa
| Air Terminal | 300.0 CMH | - | - | - | - | - | - | 0.000 Pa
216 | Duct | 250.0 CMH | 250 mmø | 1.4 m/s | - | 2975 | - | 0.13 Pa/m | 0.377 Pa | 181.977 Pa
| Fittings | 250.0 CMH | - | 1.4 m/s | 1.203 Pa | - | 150.8978 | - | 181.600 Pa
| Air Terminal | 250.0 CMH | - | - | - | - | - | - | 0.000 Pa
Critical Path : 135-136-137-93-94-95-96-97-98-99-100-86-87-88-89-90-91-48-49-50-51-52-2-1 ; Total Pressure Loss : 613.448 Pa
Detail Information of Straight Segment by Sections
Section | Element ID | Flow | Size | Velocity | Velocity Pressure | Length | Pressure Loss | Total Pressure Loss
1 | 2505372 | 13549.6 CMH | 1850 mmx1160 mm | 1.8 m/s | 1.850 Pa | 903 | 0.019 Pa | 0.019 Pa
2 | 191760 | 13549.6 CMH | 1000 mmx1000 mm | 3.8 m/s | 8.518 Pa | 1500 | 0.201 Pa | 3.087 Pa
| 191802 | 13549.6 CMH | 1000 mmx1000 mm | 3.8 m/s | 8.518 Pa | 750 | 0.100 Pa
| 192078 | 13549.6 CMH | 1000 mmx1000 mm | 3.8 m/s | 8.518 Pa | 1500 | 0.201 Pa
| 192126 | 13549.6 CMH | 1000 mmx1000 mm | 3.8 m/s | 8.518 Pa | 1500 | 0.201 Pa
| 192398 | 13549.6 CMH | 1000 mmx1000 mm | 3.8 m/s | 8.518 Pa | 1500 | 0.201 Pa
| 192440 | 13549.6 CMH | 1000 mmx1000 mm | 3.8 m/s | 8.518 Pa | 1500 | 0.201 Pa
| 192450 | 13549.6 CMH | 1000 mmx1000 mm | 3.8 m/s | 8.518 Pa | 1500 | 0.201 Pa
| 192644 | 13549.6 CMH | 1000 mmx1000 mm | 3.8 m/s | 8.518 Pa | 1500 | 0.201 Pa
| 193054 | 13549.6 CMH | 1000 mmx1000 mm | 3.8 m/s | 8.518 Pa | 1500 | 0.201 Pa
| 193056 | 13549.6 CMH | 1000 mmx1000 mm | 3.8 m/s | 8.518 Pa | 592 | 0.079 Pa
| 193206 | 13549.6 CMH | 1000 mmx1000 mm | 3.8 m/s | 8.518 Pa | 1174 | 0.157 Pa
| 193274 | 13549.6 CMH | 1000 mmx1000 mm | 3.8 m/s | 8.518 Pa | 386 | 0.052 Pa
| 193584 | 13549.6 CMH | 1000 mmx1000 mm | 3.8 m/s | 8.518 Pa | 1500 | 0.201 Pa
| 193700 | 13549.6 CMH | 1000 mmx1000 mm | 3.8 m/s | 8.518 Pa | 1500 | 0.201 Pa
| 193782 | 13549.6 CMH | 1000 mmx1000 mm | 3.8 m/s | 8.518 Pa | 1500 | 0.201 Pa
| 194114 | 13549.6 CMH | 1000 mmx1000 mm | 3.8 m/s | 8.518 Pa | 1500 | 0.201 Pa
| 194174 | 13549.6 CMH | 1000 mmx1000 mm | 3.8 m/s | 8.518 Pa | 1000 | 0.134 Pa
| 2505517 | 13549.6 CMH | 1000 mmx1000 mm | 3.8 m/s | 8.518 Pa | 1160 | 0.155 Pa
3 | 156337 | 250.0 CMH | 250 mmø | 1.4 m/s | 1.203 Pa | 25 | 0.003 Pa | 0.024 Pa
| 159784 | 250.0 CMH | 250 mmø | 1.4 m/s | 1.203 Pa | 165 | 0.021 Pa
4 | 157069 | 500.0 CMH | 250 mmø | 2.8 m/s | 4.814 Pa | 3858 | 1.687 Pa | 2.084 Pa
| 157657 | 500.0 CMH | 250 mmø | 2.8 m/s | 4.814 Pa | 132 | 0.058 Pa
| 157900 | 500.0 CMH | 250 mmø | 2.8 m/s | 4.814 Pa | 776 | 0.339 Pa
5 | 156268 | 650.0 CMH | 250 mmø | 3.7 m/s | 8.135 Pa | 1604 | 1.126 Pa | 5.825 Pa
| 156385 | 650.0 CMH | 250 mmø | 3.7 m/s | 8.135 Pa | 6145 | 4.315 Pa
| 156475 | 650.0 CMH | 250 mmø | 3.7 m/s | 8.135 Pa | 91 | 0.064 Pa
| 157408 | 650.0 CMH | 250 mmø | 3.7 m/s | 8.135 Pa | 241 | 0.169 Pa
| 159481 | 650.0 CMH | 250 mmø | 3.7 m/s | 8.135 Pa | 215 | 0.151 Pa
6 | 2261434 | 1050.0 CMH | 315 mmø | 3.7 m/s | 8.423 Pa | 3279 | 1.780 Pa | 1.780 Pa
7 | 156937 | 1200.0 CMH | 315 mmø | 4.3 m/s | 11.001 Pa | 3562 | 2.464 Pa | 9.010 Pa
| 157225 | 1200.0 CMH | 315 mmø | 4.3 m/s | 11.001 Pa | 483 | 0.334 Pa
| 158014 | 1200.0 CMH | 315 mmø | 4.3 m/s | 11.001 Pa | 487 | 0.337 Pa
| 158449 | 1200.0 CMH | 315 mmø | 4.3 m/s | 11.001 Pa | 328 | 0.227 Pa
| 158551 | 1200.0 CMH | 315 mmø | 4.3 m/s | 11.001 Pa | 4403 | 3.046 Pa
| 158869 | 1200.0 CMH | 315 mmø | 4.3 m/s | 11.001 Pa | 2250 | 1.556 Pa
| 159451 | 1200.0 CMH | 315 mmø | 4.3 m/s | 11.001 Pa | 314 | 0.217 Pa
| 2175975 | 1200.0 CMH | 315 mmø | 4.3 m/s | 11.001 Pa | 1199 | 0.829 Pa
8 | 190672 | 2050.0 CMH | 350 mmx350 mm | 4.6 m/s | 12.994 Pa | 275 | 0.194 Pa | 0.194 Pa
9 | 194708 | 2050.0 CMH | 400 mmx400 mm | 3.6 m/s | 7.617 Pa | 411 | 0.151 Pa | 0.238 Pa
| 195046 | 2050.0 CMH | 400 mmx400 mm | 3.6 m/s | 7.617 Pa | 235 | 0.087 Pa
10 | 195046 | 2400.0 CMH | 400 mmx400 mm | 4.2 m/s | 10.439 Pa | 235 | 0.115 Pa | 0.115 Pa
11 | 190134 | 2400.0 CMH | 400 mmx400 mm | 4.2 m/s | 10.439 Pa | 140 | 0.068 Pa | 2.982 Pa
| 190294 | 2400.0 CMH | 400 mmx400 mm | 4.2 m/s | 10.439 Pa | 211 | 0.103 Pa
| 190314 | 2400.0 CMH | 400 mmx400 mm | 4.2 m/s | 10.439 Pa | 619 | 0.303 Pa
| 190352 | 2400.0 CMH | 400 mmx400 mm | 4.2 m/s | 10.439 Pa | 800 | 0.391 Pa
| 190728 | 2400.0 CMH | 400 mmx400 mm | 4.2 m/s | 10.439 Pa | 312 | 0.153 Pa
| 193596 | 2400.0 CMH | 400 mmx400 mm | 4.2 m/s | 10.439 Pa | 1197 | 0.586 Pa
| 194292 | 2400.0 CMH | 400 mmx400 mm | 4.2 m/s | 10.439 Pa | 437 | 0.214 Pa
| 194876 | 2400.0 CMH | 400 mmx400 mm | 4.2 m/s | 10.439 Pa | 1500 | 0.734 Pa
| 195288 | 2400.0 CMH | 400 mmx400 mm | 4.2 m/s | 10.439 Pa | 879 | 0.430 Pa
12 | 191910 | 2400.0 CMH | 600 mmx600 mm | 1.9 m/s | 2.062 Pa | 855 | 0.059 Pa | 0.059 Pa
13 | 191472 | 4850.0 CMH | 600 mmx600 mm | 3.7 m/s | 8.421 Pa | 1500 | 0.368 Pa | 0.723 Pa
| 191910 | 4850.0 CMH | 600 mmx600 mm | 3.7 m/s | 8.421 Pa | 645 | 0.158 Pa
| 194474 | 4850.0 CMH | 600 mmx600 mm | 3.7 m/s | 8.421 Pa | 800 | 0.196 Pa
14 | 191202 | 4850.0 CMH | 700 mmx700 mm | 2.7 m/s | 4.546 Pa | 855 | 0.099 Pa | 0.099 Pa
15 | 191202 | 7200.0 CMH | 700 mmx700 mm | 4.1 m/s | 10.018 Pa | 645 | 0.154 Pa | 1.747 Pa
| 191532 | 7200.0 CMH | 700 mmx700 mm | 4.1 m/s | 10.018 Pa | 1000 | 0.239 Pa
| 192166 | 7200.0 CMH | 700 mmx700 mm | 4.1 m/s | 10.018 Pa | 200 | 0.048 Pa
| 192856 | 7200.0 CMH | 700 mmx700 mm | 4.1 m/s | 10.018 Pa | 1500 | 0.359 Pa
| 193186 | 7200.0 CMH | 700 mmx700 mm | 4.1 m/s | 10.018 Pa | 600 | 0.143 Pa
| 193280 | 7200.0 CMH | 700 mmx700 mm | 4.1 m/s | 10.018 Pa | 1500 | 0.359 Pa
| 193292 | 7200.0 CMH | 700 mmx700 mm | 4.1 m/s | 10.018 Pa | 1500 | 0.359 Pa
| 193694 | 7200.0 CMH | 700 mmx700 mm | 4.1 m/s | 10.018 Pa | 364 | 0.087 Pa
16 | 191638 | 7200.0 CMH | 1000 mmx500 mm | 4.0 m/s | 9.621 Pa | 1500 | 0.366 Pa | 2.785 Pa
| 192272 | 7200.0 CMH | 1000 mmx500 mm | 4.0 m/s | 9.621 Pa | 1230 | 0.301 Pa
| 192596 | 7200.0 CMH | 500 mmx1000 mm | 4.0 m/s | 9.621 Pa | 700 | 0.171 Pa
| 192864 | 7200.0 CMH | 1000 mmx500 mm | 4.0 m/s | 9.621 Pa | 1500 | 0.366 Pa
| 192912 | 7200.0 CMH | 1000 mmx500 mm | 4.0 m/s | 9.621 Pa | 139 | 0.034 Pa
| 193122 | 7200.0 CMH | 1000 mmx500 mm | 4.0 m/s | 9.621 Pa | 1500 | 0.366 Pa
| 193166 | 7200.0 CMH | 1000 mmx500 mm | 4.0 m/s | 9.621 Pa | 330 | 0.081 Pa
| 193490 | 7200.0 CMH | 1000 mmx500 mm | 4.0 m/s | 9.621 Pa | 1500 | 0.366 Pa
| 193876 | 7200.0 CMH | 1000 mmx500 mm | 4.0 m/s | 9.621 Pa | 1500 | 0.366 Pa
| 194352 | 7200.0 CMH | 1000 mmx500 mm | 4.0 m/s | 9.621 Pa | 1500 | 0.366 Pa
17 | 193796 | 7200.0 CMH | 1000 mmx500 mm | 4.0 m/s | 9.621 Pa | 200 | 0.049 Pa | 0.234 Pa
| 194338 | 7200.0 CMH | 1000 mmx500 mm | 4.0 m/s | 9.621 Pa | 758 | 0.185 Pa
18 | 191706 | 7200.0 CMH | 1000 mmx500 mm | 4.0 m/s | 9.621 Pa | 827 | 0.202 Pa | 0.496 Pa
| 191850 | 7200.0 CMH | 1000 mmx500 mm | 4.0 m/s | 9.621 Pa | 961 | 0.235 Pa
| 193980 | 7200.0 CMH | 1000 mmx500 mm | 4.0 m/s | 9.621 Pa | 242 | 0.059 Pa
19 | 191802 | 7200.0 CMH | 1000 mmx1000 mm | 2.0 m/s | 2.405 Pa | 750 | 0.031 Pa | 0.054 Pa
| 193776 | 7200.0 CMH | 1000 mmx1000 mm | 2.0 m/s | 2.405 Pa | 539 | 0.023 Pa
20 | 157465 | 100.0 CMH | 160 mmø | 1.4 m/s | 1.148 Pa | 111 | 0.024 Pa | 0.284 Pa
| 157624 | 100.0 CMH | 160 mmø | 1.4 m/s | 1.148 Pa | 393 | 0.083 Pa
| 158020 | 100.0 CMH | 160 mmø | 1.4 m/s | 1.148 Pa | 580 | 0.123 Pa
| 158725 | 100.0 CMH | 160 mmø | 1.4 m/s | 1.148 Pa | 169 | 0.036 Pa
| 159445 | 100.0 CMH | 160 mmø | 1.4 m/s | 1.148 Pa | 84 | 0.018 Pa
21 | 158398 | 350.0 CMH | 250 mmø | 2.0 m/s | 2.359 Pa | 1403 | 0.323 Pa | 0.583 Pa
| 159034 | 350.0 CMH | 250 mmø | 2.0 m/s | 2.359 Pa | 558 | 0.129 Pa
| 159070 | 350.0 CMH | 250 mmø | 2.0 m/s | 2.359 Pa | 284 | 0.065 Pa
| 159598 | 350.0 CMH | 250 mmø | 2.0 m/s | 2.359 Pa | 284 | 0.065 Pa
22 | 156376 | 500.0 CMH | 250 mmø | 2.8 m/s | 4.814 Pa | 496 | 0.217 Pa | 1.242 Pa
| 159391 | 500.0 CMH | 250 mmø | 2.8 m/s | 4.814 Pa | 2344 | 1.025 Pa
23 | 156223 | 600.0 CMH | 250 mmø | 3.4 m/s | 6.932 Pa | 1398 | 0.849 Pa | 4.669 Pa
| 156922 | 600.0 CMH | 250 mmø | 3.4 m/s | 6.932 Pa | 2473 | 1.502 Pa
| 158746 | 600.0 CMH | 250 mmø | 3.4 m/s | 6.932 Pa | 2717 | 1.650 Pa
| 159862 | 600.0 CMH | 250 mmø | 3.4 m/s | 6.932 Pa | 147 | 0.090 Pa
| 2235276 | 600.0 CMH | 250 mmø | 3.4 m/s | 6.932 Pa | 950 | 0.577 Pa
24 | 2234245 | 850.0 CMH | 280 mmø | 3.8 m/s | 8.841 Pa | 98 | 0.064 Pa | 0.064 Pa
25 | 190672 | 850.0 CMH | 350 mmx350 mm | 1.9 m/s | 2.234 Pa | 193 | 0.028 Pa | 0.028 Pa
26 | 157075 | 150.0 CMH | 160 mmø | 2.1 m/s | 2.582 Pa | 336 | 0.147 Pa | 0.546 Pa
| 157585 | 150.0 CMH | 160 mmø | 2.1 m/s | 2.582 Pa | 160 | 0.070 Pa
| 158491 | 150.0 CMH | 160 mmø | 2.1 m/s | 2.582 Pa | 165 | 0.072 Pa
| 159643 | 150.0 CMH | 160 mmø | 2.1 m/s | 2.582 Pa | 589 | 0.257 Pa
27 | 157033 | 100.0 CMH | 160 mmø | 1.4 m/s | 1.148 Pa | 580 | 0.123 Pa | 0.283 Pa
| 157399 | 100.0 CMH | 160 mmø | 1.4 m/s | 1.148 Pa | 169 | 0.036 Pa
| 157510 | 100.0 CMH | 160 mmø | 1.4 m/s | 1.148 Pa | 128 | 0.027 Pa
| 158509 | 100.0 CMH | 160 mmø | 1.4 m/s | 1.148 Pa | 321 | 0.068 Pa
| 158992 | 100.0 CMH | 160 mmø | 1.4 m/s | 1.148 Pa | 137 | 0.029 Pa
28 | 157354 | 250.0 CMH | 250 mmø | 1.4 m/s | 1.203 Pa | 250 | 0.032 Pa | 0.225 Pa
| 157387 | 250.0 CMH | 250 mmø | 1.4 m/s | 1.203 Pa | 357 | 0.045 Pa
| 157396 | 250.0 CMH | 250 mmø | 1.4 m/s | 1.203 Pa | 116 | 0.015 Pa
| 157918 | 250.0 CMH | 250 mmø | 1.4 m/s | 1.203 Pa | 191 | 0.024 Pa
| 158569 | 250.0 CMH | 250 mmø | 1.4 m/s | 1.203 Pa | 367 | 0.046 Pa
| 158950 | 250.0 CMH | 250 mmø | 1.4 m/s | 1.203 Pa | 167 | 0.021 Pa
| 159340 | 250.0 CMH | 250 mmø | 1.4 m/s | 1.203 Pa | 71 | 0.009 Pa
| 460683 | 250.0 CMH | 250 mmø | 1.4 m/s | 1.203 Pa | 257 | 0.032 Pa
29 | 158959 | 125.0 CMH | 160 mmø | 1.7 m/s | 1.793 Pa | 3095 | 0.976 Pa | 0.976 Pa
30 | 157492 | 250.0 CMH | 160 mmø | 3.5 m/s | 7.173 Pa | 2601 | 2.847 Pa | 4.075 Pa
| 157717 | 250.0 CMH | 160 mmø | 3.5 m/s | 7.173 Pa | 122 | 0.133 Pa
| 158572 | 250.0 CMH | 160 mmø | 3.5 m/s | 7.173 Pa | 1000 | 1.095 Pa
32 | 156472 | 150.0 CMH | 160 mmø | 2.1 m/s | 2.582 Pa | 143 | 0.062 Pa | 0.518 Pa
| 157654 | 150.0 CMH | 160 mmø | 2.1 m/s | 2.582 Pa | 192 | 0.084 Pa
| 158803 | 150.0 CMH | 160 mmø | 2.1 m/s | 2.582 Pa | 652 | 0.285 Pa
| 159151 | 150.0 CMH | 160 mmø | 2.1 m/s | 2.582 Pa | 199 | 0.087 Pa
34 | 156244 | 400.0 CMH | 250 mmø | 2.3 m/s | 3.081 Pa | 257 | 0.075 Pa | 2.635 Pa
| 157015 | 400.0 CMH | 250 mmø | 2.3 m/s | 3.081 Pa | 2636 | 0.772 Pa
| 157534 | 400.0 CMH | 250 mmø | 2.3 m/s | 3.081 Pa | 353 | 0.103 Pa
| 157753 | 400.0 CMH | 250 mmø | 2.3 m/s | 3.081 Pa | 1124 | 0.329 Pa
| 158026 | 400.0 CMH | 250 mmø | 2.3 m/s | 3.081 Pa | 2347 | 0.687 Pa
| 159538 | 400.0 CMH | 250 mmø | 2.3 m/s | 3.081 Pa | 658 | 0.193 Pa
| 159730 | 400.0 CMH | 250 mmø | 2.3 m/s | 3.081 Pa | 1368 | 0.401 Pa
| 460640 | 400.0 CMH | 250 mmø | 2.3 m/s | 3.081 Pa | 255 | 0.075 Pa
36 | 156478 | 150.0 CMH | 160 mmø | 2.1 m/s | 2.582 Pa | 329 | 0.144 Pa | 1.344 Pa
| 156493 | 150.0 CMH | 160 mmø | 2.1 m/s | 2.582 Pa | 221 | 0.097 Pa
| 156520 | 150.0 CMH | 160 mmø | 2.1 m/s | 2.582 Pa | 40 | 0.018 Pa
| 157429 | 150.0 CMH | 160 mmø | 2.1 m/s | 2.582 Pa | 256 | 0.112 Pa
| 157978 | 150.0 CMH | 160 mmø | 2.1 m/s | 2.582 Pa | 356 | 0.156 Pa
| 158533 | 150.0 CMH | 160 mmø | 2.1 m/s | 2.582 Pa | 400 | 0.175 Pa
| 158650 | 150.0 CMH | 160 mmø | 2.1 m/s | 2.582 Pa | 880 | 0.384 Pa
| 159349 | 150.0 CMH | 160 mmø | 2.1 m/s | 2.582 Pa | 596 | 0.260 Pa
37 | 160696 | 200.0 CMH | 160 mmø | 2.8 m/s | 4.591 Pa | 264 | 0.193 Pa | 0.483 Pa
| 162301 | 200.0 CMH | 160 mmø | 2.8 m/s | 4.591 Pa | 206 | 0.151 Pa
| 163009 | 200.0 CMH | 160 mmø | 2.8 m/s | 4.591 Pa | 189 | 0.138 Pa
38 | 159919 | 400.0 CMH | 180 mmø | 4.4 m/s | 11.464 Pa | 185 | 0.268 Pa | 18.005 Pa
| 160384 | 400.0 CMH | 180 mmø | 4.4 m/s | 11.464 Pa | 95 | 0.137 Pa
| 160570 | 400.0 CMH | 180 mmø | 4.4 m/s | 11.464 Pa | 295 | 0.427 Pa
| 160645 | 400.0 CMH | 180 mmø | 4.4 m/s | 11.464 Pa | 1651 | 2.387 Pa
| 160843 | 400.0 CMH | 180 mmø | 4.4 m/s | 11.464 Pa | 361 | 0.522 Pa
| 161488 | 400.0 CMH | 180 mmø | 4.4 m/s | 11.464 Pa | 373 | 0.540 Pa
| 161995 | 400.0 CMH | 180 mmø | 4.4 m/s | 11.464 Pa | 2885 | 4.171 Pa
| 162142 | 400.0 CMH | 180 mmø | 4.4 m/s | 11.464 Pa | 298 | 0.430 Pa
| 162163 | 400.0 CMH | 180 mmø | 4.4 m/s | 11.464 Pa | 10 | 0.014 Pa
| 162205 | 400.0 CMH | 180 mmø | 4.4 m/s | 11.464 Pa | 311 | 0.449 Pa
| 163156 | 400.0 CMH | 180 mmø | 4.4 m/s | 11.464 Pa | 108 | 0.156 Pa
| 163249 | 400.0 CMH | 180 mmø | 4.4 m/s | 11.464 Pa | 1605 | 2.319 Pa
| 163300 | 400.0 CMH | 180 mmø | 4.4 m/s | 11.464 Pa | 3740 | 5.406 Pa
| 1722201 | 400.0 CMH | 180 mmø | 4.4 m/s | 11.464 Pa | 539 | 0.779 Pa
40 | 161068 | 800.0 CMH | 250 mmø | 4.5 m/s | 12.323 Pa | 2312 | 2.367 Pa | 6.986 Pa
| 162547 | 800.0 CMH | 250 mmø | 4.5 m/s | 12.323 Pa | 945 | 0.968 Pa
| 163069 | 800.0 CMH | 250 mmø | 4.5 m/s | 12.323 Pa | 259 | 0.265 Pa
| 163318 | 800.0 CMH | 250 mmø | 4.5 m/s | 12.323 Pa | 188 | 0.192 Pa
| 1772478 | 800.0 CMH | 250 mmø | 4.5 m/s | 12.323 Pa | 3119 | 3.194 Pa
41 | 2236144 | 800.0 CMH | 280 mmø | 3.6 m/s | 7.832 Pa | 135 | 0.079 Pa | 0.079 Pa
42 | 159904 | 950.0 CMH | 280 mmø | 4.3 m/s | 11.044 Pa | 3700 | 2.976 Pa | 11.377 Pa
| 160324 | 950.0 CMH | 280 mmø | 4.3 m/s | 11.044 Pa | 135 | 0.109 Pa
| 160342 | 950.0 CMH | 280 mmø | 4.3 m/s | 11.044 Pa | 3483 | 2.801 Pa
| 160345 | 950.0 CMH | 280 mmø | 4.3 m/s | 11.044 Pa | 219 | 0.176 Pa
| 160378 | 950.0 CMH | 280 mmø | 4.3 m/s | 11.044 Pa | 506 | 0.407 Pa
| 161080 | 950.0 CMH | 280 mmø | 4.3 m/s | 11.044 Pa | 4967 | 3.995 Pa
| 163438 | 950.0 CMH | 280 mmø | 4.3 m/s | 11.044 Pa | 1000 | 0.804 Pa
| 1803662 | 950.0 CMH | 280 mmø | 4.3 m/s | 11.044 Pa | 135 | 0.109 Pa
43 | 189948 | 2100.0 CMH | 400 mmx400 mm | 3.6 m/s | 7.993 Pa | 166 | 0.064 Pa | 0.142 Pa
| 193998 | 2100.0 CMH | 400 mmx400 mm | 3.6 m/s | 7.993 Pa | 203 | 0.078 Pa
44 | 194632 | 2100.0 CMH | 400 mmx400 mm | 3.6 m/s | 7.993 Pa | 215 | 0.083 Pa | 0.083 Pa
45 | 191148 | 2350.0 CMH | 400 mmx400 mm | 4.1 m/s | 10.009 Pa | 1000 | 0.471 Pa | 1.207 Pa
| 191630 | 2350.0 CMH | 400 mmx400 mm | 4.1 m/s | 10.009 Pa | 1039 | 0.489 Pa
| 192882 | 2350.0 CMH | 400 mmx400 mm | 4.1 m/s | 10.009 Pa | 79 | 0.037 Pa
| 194632 | 2350.0 CMH | 400 mmx400 mm | 4.1 m/s | 10.009 Pa | 445 | 0.209 Pa
46 | 191898 | 2350.0 CMH | 450 mmx450 mm | 3.2 m/s | 6.249 Pa | 123 | 0.033 Pa | 0.214 Pa
| 191980 | 2350.0 CMH | 450 mmx450 mm | 3.2 m/s | 6.249 Pa | 684 | 0.181 Pa
47 | 174643 | 250.0 CMH | 250 mmø | 1.4 m/s | 1.203 Pa | 629 | 0.080 Pa | 0.385 Pa
| 175297 | 250.0 CMH | 250 mmø | 1.4 m/s | 1.203 Pa | 1183 | 0.150 Pa
| 175351 | 250.0 CMH | 250 mmø | 1.4 m/s | 1.203 Pa | 756 | 0.096 Pa
| 176293 | 250.0 CMH | 250 mmø | 1.4 m/s | 1.203 Pa | 348 | 0.044 Pa
| 2177309 | 250.0 CMH | 250 mmø | 1.4 m/s | 1.203 Pa | 124 | 0.016 Pa
48 | 190040 | 2499.8 CMH | 400 mmx400 mm | 4.3 m/s | 11.326 Pa | 309 | 0.163 Pa | 3.286 Pa
| 193226 | 2499.8 CMH | 400 mmx400 mm | 4.3 m/s | 11.326 Pa | 1500 | 0.790 Pa
| 193428 | 2499.8 CMH | 400 mmx400 mm | 4.3 m/s | 11.326 Pa | 1378 | 0.726 Pa
| 194182 | 2499.8 CMH | 400 mmx400 mm | 4.3 m/s | 11.326 Pa | 1500 | 0.790 Pa
| 194796 | 2499.8 CMH | 400 mmx400 mm | 4.3 m/s | 11.326 Pa | 1550 | 0.817 Pa
49 | 193710 | 2499.8 CMH | 400 mmx400 mm | 4.3 m/s | 11.326 Pa | 67 | 0.035 Pa | 0.035 Pa
50 | 190810 | 4099.8 CMH | 500 mmx500 mm | 4.6 m/s | 12.478 Pa | 620 | 0.273 Pa | 0.845 Pa
| 194890 | 4099.8 CMH | 500 mmx500 mm | 4.6 m/s | 12.478 Pa | 1300 | 0.572 Pa
51 | 190090 | 4099.8 CMH | 600 mmx600 mm | 3.2 m/s | 6.017 Pa | 914 | 0.165 Pa | 0.345 Pa
| 195414 | 4099.8 CMH | 600 mmx600 mm | 3.2 m/s | 6.017 Pa | 1000 | 0.180 Pa
52 | 190090 | 6349.6 CMH | 600 mmx600 mm | 4.9 m/s | 14.434 Pa | 586 | 0.237 Pa | 6.070 Pa
| 191382 | 6349.6 CMH | 600 mmx600 mm | 4.9 m/s | 14.434 Pa | 468 | 0.189 Pa
| 191894 | 6349.6 CMH | 600 mmx600 mm | 4.9 m/s | 14.434 Pa | 1200 | 0.485 Pa
| 192120 | 6349.6 CMH | 600 mmx600 mm | 4.9 m/s | 14.434 Pa | 1084 | 0.438 Pa
| 192370 | 6349.6 CMH | 600 mmx600 mm | 4.9 m/s | 14.434 Pa | 510 | 0.206 Pa
| 192520 | 6349.6 CMH | 600 mmx600 mm | 4.9 m/s | 14.434 Pa | 1400 | 0.565 Pa
| 192526 | 6349.6 CMH | 600 mmx600 mm | 4.9 m/s | 14.434 Pa | 1301 | 0.526 Pa
| 192832 | 6349.6 CMH | 600 mmx600 mm | 4.9 m/s | 14.434 Pa | 552 | 0.223 Pa
| 192966 | 6349.6 CMH | 600 mmx600 mm | 4.9 m/s | 14.434 Pa | 1500 | 0.606 Pa
| 192968 | 6349.6 CMH | 600 mmx600 mm | 4.9 m/s | 14.434 Pa | 561 | 0.227 Pa
| 193466 | 6349.6 CMH | 600 mmx600 mm | 4.9 m/s | 14.434 Pa | 1500 | 0.606 Pa
| 194076 | 6349.6 CMH | 600 mmx600 mm | 4.9 m/s | 14.434 Pa | 1500 | 0.606 Pa
| 194204 | 6349.6 CMH | 600 mmx600 mm | 4.9 m/s | 14.434 Pa | 1318 | 0.532 Pa
| 194378 | 6349.6 CMH | 600 mmx600 mm | 4.9 m/s | 14.434 Pa | 1500 | 0.606 Pa
| 2178969 | 6349.6 CMH | 600 mmx600 mm | 4.9 m/s | 14.434 Pa | 47 | 0.019 Pa
53 | 160405 | 250.0 CMH | 250 mmø | 1.4 m/s | 1.203 Pa | 1179 | 0.149 Pa | 0.212 Pa
| 160408 | 250.0 CMH | 250 mmø | 1.4 m/s | 1.203 Pa | 150 | 0.019 Pa
| 162895 | 250.0 CMH | 250 mmø | 1.4 m/s | 1.203 Pa | 111 | 0.014 Pa
| 163168 | 250.0 CMH | 250 mmø | 1.4 m/s | 1.203 Pa | 232 | 0.029 Pa
54 | 160276 | 500.0 CMH | 250 mmø | 2.8 m/s | 4.814 Pa | 94 | 0.041 Pa | 2.361 Pa
| 160540 | 500.0 CMH | 250 mmø | 2.8 m/s | 4.814 Pa | 683 | 0.299 Pa
| 160576 | 500.0 CMH | 250 mmø | 2.8 m/s | 4.814 Pa | 328 | 0.143 Pa
| 161944 | 500.0 CMH | 250 mmø | 2.8 m/s | 4.814 Pa | 2897 | 1.267 Pa
| 162031 | 500.0 CMH | 250 mmø | 2.8 m/s | 4.814 Pa | 1135 | 0.496 Pa
| 162910 | 500.0 CMH | 250 mmø | 2.8 m/s | 4.814 Pa | 264 | 0.115 Pa
55 | 161947 | 600.0 CMH | 250 mmø | 3.4 m/s | 6.932 Pa | 3190 | 1.938 Pa | 1.938 Pa
56 | 163003 | 750.0 CMH | 250 mmø | 4.2 m/s | 10.831 Pa | 3187 | 2.902 Pa | 2.902 Pa
57 | 160714 | 850.0 CMH | 250 mmø | 4.8 m/s | 13.912 Pa | 383 | 0.438 Pa | 0.438 Pa
58 | 192470 | 850.0 CMH | 300 mmx300 mm | 2.6 m/s | 4.139 Pa | 1500 | 0.456 Pa | 0.857 Pa
| 192700 | 850.0 CMH | 300 mmx300 mm | 2.6 m/s | 4.139 Pa | 1320 | 0.401 Pa
59 | 191116 | 1000.0 CMH | 300 mmx300 mm | 3.1 m/s | 5.728 Pa | 875 | 0.356 Pa | 0.429 Pa
| 192700 | 1000.0 CMH | 300 mmx300 mm | 3.1 m/s | 5.728 Pa | 180 | 0.073 Pa
60 | 191116 | 1150.0 CMH | 300 mmx300 mm | 3.5 m/s | 7.575 Pa | 625 | 0.328 Pa | 0.711 Pa
| 192446 | 1150.0 CMH | 300 mmx300 mm | 3.5 m/s | 7.575 Pa | 731 | 0.383 Pa
61 | 189672 | 1150.0 CMH | 350 mmx200 mm | 4.6 m/s | 12.523 Pa | 500 | 0.508 Pa | 0.508 Pa
62 | 190296 | 1150.0 CMH | 350 mmx200 mm | 4.6 m/s | 12.523 Pa | 235 | 0.239 Pa | 1.719 Pa
| 193504 | 1150.0 CMH | 350 mmx200 mm | 4.6 m/s | 12.523 Pa | 1457 | 1.480 Pa
63 | 192148 | 1150.0 CMH | 400 mmx400 mm | 2.0 m/s | 2.397 Pa | 111 | 0.014 Pa | 0.053 Pa
| 193998 | 1150.0 CMH | 400 mmx400 mm | 2.0 m/s | 2.397 Pa | 297 | 0.039 Pa
64 | 173023 | 150.0 CMH | 160 mmø | 2.1 m/s | 2.582 Pa | 614 | 0.268 Pa | 0.858 Pa
| 173881 | 150.0 CMH | 160 mmø | 2.1 m/s | 2.582 Pa | 259 | 0.113 Pa
| 174262 | 150.0 CMH | 160 mmø | 2.1 m/s | 2.582 Pa | 82 | 0.036 Pa
| 174466 | 150.0 CMH | 160 mmø | 2.1 m/s | 2.582 Pa | 700 | 0.306 Pa
| 1722604 | 150.0 CMH | 160 mm | 2.1 m/s | 2.582 Pa | 310 | 0.136 Pa
65 | 2214140 | 900.0 CMH | 280 mmø | 4.1 m/s | 9.912 Pa | 1140 | 0.831 Pa | 0.831 Pa
66 | 172927 | 900.0 CMH | 280 mmø | 4.1 m/s | 9.912 Pa | 2428 | 1.770 Pa | 2.194 Pa
| 173095 | 900.0 CMH | 280 mmø | 4.1 m/s | 9.912 Pa | 146 | 0.107 Pa
| 173452 | 900.0 CMH | 280 mmø | 4.1 m/s | 9.912 Pa | 114 | 0.083 Pa
| 174154 | 900.0 CMH | 280 mmø | 4.1 m/s | 9.912 Pa | 322 | 0.235 Pa
67 | 189530 | 900.0 CMH | 400 mmx400 mm | 1.6 m/s | 1.468 Pa | 414 | 0.035 Pa | 0.035 Pa
68 | 189530 | 2200.0 CMH | 400 mmx400 mm | 3.8 m/s | 8.772 Pa | 415 | 0.173 Pa | 0.173 Pa
69 | 189530 | 2450.0 CMH | 400 mmx400 mm | 4.3 m/s | 10.879 Pa | 148 | 0.075 Pa | 1.663 Pa
| 190450 | 2450.0 CMH | 400 mmx400 mm | 4.3 m/s | 10.879 Pa | 620 | 0.315 Pa
| 194800 | 2450.0 CMH | 400 mmx400 mm | 4.3 m/s | 10.879 Pa | 1500 | 0.762 Pa
| 194930 | 2450.0 CMH | 400 mmx400 mm | 4.3 m/s | 10.879 Pa | 107 | 0.054 Pa
| 1746718 | 2450.0 CMH | 400 mmx400 mm | 4.3 m/s | 10.879 Pa | 900 | 0.457 Pa
70 | 195074 | 2450.0 CMH | 450 mmx450 mm | 3.4 m/s | 6.792 Pa | 655 | 0.187 Pa | 0.244 Pa
| 195372 | 2450.0 CMH | 450 mmx450 mm | 3.4 m/s | 6.792 Pa | 198 | 0.057 Pa
71 | 174745 | 150.0 CMH | 160 mmø | 2.1 m/s | 2.582 Pa | 217 | 0.095 Pa | 0.676 Pa
| 175225 | 150.0 CMH | 160 mmø | 2.1 m/s | 2.582 Pa | 80 | 0.035 Pa
| 1712838 | 150.0 CMH | 160 mm | 2.1 m/s | 2.582 Pa | 375 | 0.164 Pa
| 1722568 | 150.0 CMH | 160 mmø | 2.1 m/s | 2.582 Pa | 260 | 0.114 Pa
| 1722574 | 150.0 CMH | 160 mmø | 2.1 m/s | 2.582 Pa | 614 | 0.268 Pa
72 | 2261620 | 750.0 CMH | 280 mmø | 3.4 m/s | 6.883 Pa | 946 | 0.495 Pa | 0.495 Pa
73 | 174178 | 100.0 CMH | 160 mmø | 1.4 m/s | 1.148 Pa | 259 | 0.055 Pa | 0.362 Pa
| 174730 | 100.0 CMH | 160 mmø | 1.4 m/s | 1.148 Pa | 365 | 0.077 Pa
| 175567 | 100.0 CMH | 160 mmø | 1.4 m/s | 1.148 Pa | 614 | 0.130 Pa
| 175966 | 100.0 CMH | 160 mmø | 1.4 m/s | 1.148 Pa | 96 | 0.020 Pa
| 1722606 | 100.0 CMH | 160 mm | 1.4 m/s | 1.148 Pa | 375 | 0.079 Pa
74 | 2214395 | 600.0 CMH | 250 mmø | 3.4 m/s | 6.932 Pa | 2592 | 1.575 Pa | 1.575 Pa
75 | 2261522 | 600.0 CMH | 280 mmø | 2.7 m/s | 4.405 Pa | 300 | 0.105 Pa | 0.105 Pa
76 | 173134 | 150.0 CMH | 160 mmø | 2.1 m/s | 2.582 Pa | 96 | 0.042 Pa | 0.747 Pa
| 173635 | 150.0 CMH | 160 mmø | 2.1 m/s | 2.582 Pa | 259 | 0.113 Pa
| 174043 | 150.0 CMH | 160 mmø | 2.1 m/s | 2.582 Pa | 368 | 0.161 Pa
| 175312 | 150.0 CMH | 160 mmø | 2.1 m/s | 2.582 Pa | 614 | 0.268 Pa
| 1722609 | 150.0 CMH | 160 mm | 2.1 m/s | 2.582 Pa | 374 | 0.163 Pa
77 | 174406 | 500.0 CMH | 250 mmø | 2.8 m/s | 4.814 Pa | 3187 | 1.393 Pa | 1.393 Pa
78 | 173434 | 100.0 CMH | 160 mmø | 1.4 m/s | 1.148 Pa | 95 | 0.020 Pa | 0.363 Pa
| 174748 | 100.0 CMH | 160 mmø | 1.4 m/s | 1.148 Pa | 368 | 0.078 Pa
| 174967 | 100.0 CMH | 160 mmø | 1.4 m/s | 1.148 Pa | 259 | 0.055 Pa
| 175894 | 100.0 CMH | 160 mmø | 1.4 m/s | 1.148 Pa | 614 | 0.130 Pa
| 1722612 | 100.0 CMH | 160 mm | 1.4 m/s | 1.148 Pa | 375 | 0.080 Pa
79 | 173053 | 350.0 CMH | 250 mmø | 2.0 m/s | 2.359 Pa | 3190 | 0.736 Pa | 0.736 Pa
80 | 173923 | 266.6 CMH | 250 mmø | 1.5 m/s | 1.369 Pa | 8348 | 1.185 Pa | 1.185 Pa
81 | 2213301 | 533.2 CMH | 250 mmø | 3.0 m/s | 5.474 Pa | 3530 | 1.733 Pa | 1.733 Pa
82 | 174784 | 799.8 CMH | 250 mmø | 4.5 m/s | 12.317 Pa | 336 | 0.344 Pa | 0.576 Pa
| 2215372 | 799.8 CMH | 250 mmø | 4.5 m/s | 12.317 Pa | 227 | 0.232 Pa
84 | 172960 | 799.8 CMH | 250 mmø | 4.5 m/s | 12.317 Pa | 57 | 0.058 Pa | 1.940 Pa
| 173086 | 799.8 CMH | 250 mmø | 4.5 m/s | 12.317 Pa | 93 | 0.095 Pa
| 173509 | 799.8 CMH | 250 mmø | 4.5 m/s | 12.317 Pa | 50 | 0.051 Pa
| 174319 | 799.8 CMH | 250 mmø | 4.5 m/s | 12.317 Pa | 367 | 0.376 Pa
| 175039 | 799.8 CMH | 250 mmø | 4.5 m/s | 12.317 Pa | 436 | 0.447 Pa
| 175561 | 799.8 CMH | 250 mmø | 4.5 m/s | 12.317 Pa | 371 | 0.380 Pa
| 175579 | 799.8 CMH | 250 mmø | 4.5 m/s | 12.317 Pa | 231 | 0.236 Pa
| 175918 | 799.8 CMH | 250 mmø | 4.5 m/s | 12.317 Pa | 290 | 0.297 Pa
85 | 194982 | 799.8 CMH | 300 mmx300 mm | 2.5 m/s | 3.664 Pa | 278 | 0.076 Pa | 0.076 Pa
86 | 189626 | 1449.8 CMH | 300 mmx300 mm | 4.5 m/s | 12.040 Pa | 1500 | 1.197 Pa | 7.932 Pa
| 190326 | 1449.8 CMH | 300 mmx300 mm | 4.5 m/s | 12.040 Pa | 1500 | 1.197 Pa
| 192204 | 1449.8 CMH | 300 mmx300 mm | 4.5 m/s | 12.040 Pa | 1500 | 1.197 Pa
| 194654 | 1449.8 CMH | 300 mmx300 mm | 4.5 m/s | 12.040 Pa | 1216 | 0.971 Pa
| 194974 | 1449.8 CMH | 300 mmx300 mm | 4.5 m/s | 12.040 Pa | 1500 | 1.197 Pa
| 194982 | 1449.8 CMH | 300 mmx300 mm | 4.5 m/s | 12.040 Pa | 1222 | 0.975 Pa
| 195060 | 1449.8 CMH | 300 mmx300 mm | 4.5 m/s | 12.040 Pa | 1500 | 1.197 Pa
87 | 189988 | 1449.8 CMH | 300 mmx300 mm | 4.5 m/s | 12.040 Pa | 117 | 0.093 Pa | 3.042 Pa
| 192784 | 1449.8 CMH | 300 mmx300 mm | 4.5 m/s | 12.040 Pa | 1500 | 1.197 Pa
| 193346 | 1449.8 CMH | 300 mmx300 mm | 4.5 m/s | 12.040 Pa | 731 | 0.583 Pa
| 195606 | 1449.8 CMH | 300 mmx300 mm | 4.5 m/s | 12.040 Pa | 1463 | 1.168 Pa
88 | 195042 | 1449.8 CMH | 400 mmx400 mm | 2.5 m/s | 3.810 Pa | 155 | 0.030 Pa | 0.030 Pa
89 | 195042 | 1749.8 CMH | 400 mmx400 mm | 3.0 m/s | 5.549 Pa | 643 | 0.178 Pa | 0.178 Pa
90 | 194912 | 2249.8 CMH | 400 mmx400 mm | 3.9 m/s | 9.174 Pa | 200 | 0.087 Pa | 0.174 Pa
| 195042 | 2249.8 CMH | 400 mmx400 mm | 3.9 m/s | 9.174 Pa | 199 | 0.087 Pa
91 | 190040 | 2249.8 CMH | 400 mmx400 mm | 3.9 m/s | 9.174 Pa | 1191 | 0.518 Pa | 0.518 Pa
92 | 174463 | 100.0 CMH | 160 mmø | 1.4 m/s | 1.148 Pa | 217 | 0.046 Pa | 0.308 Pa
| 176137 | 100.0 CMH | 160 mmø | 1.4 m/s | 1.148 Pa | 305 | 0.065 Pa
| 176266 | 100.0 CMH | 160 mmø | 1.4 m/s | 1.148 Pa | 637 | 0.135 Pa
| 1607289 | 100.0 CMH | 160 mm | 1.4 m/s | 1.148 Pa | 296 | 0.063 Pa
93 | 189936 | 350.0 CMH | 200 mmx200 mm | 2.4 m/s | 3.552 Pa | 156 | 0.069 Pa | 1.517 Pa
| 191558 | 350.0 CMH | 200 mmx200 mm | 2.4 m/s | 3.552 Pa | 750 | 0.330 Pa
| 193066 | 350.0 CMH | 200 mmx200 mm | 2.4 m/s | 3.552 Pa | 597 | 0.263 Pa
| 194276 | 350.0 CMH | 200 mmx200 mm | 2.4 m/s | 3.552 Pa | 250 | 0.110 Pa
| 194660 | 350.0 CMH | 200 mmx200 mm | 2.4 m/s | 3.552 Pa | 1000 | 0.440 Pa
| 195444 | 350.0 CMH | 200 mmx200 mm | 2.4 m/s | 3.552 Pa | 697 | 0.306 Pa
94 | 189734 | 450.0 CMH | 200 mmx200 mm | 3.1 m/s | 5.872 Pa | 547 | 0.378 Pa | 2.384 Pa
| 191886 | 450.0 CMH | 200 mmx200 mm | 3.1 m/s | 5.872 Pa | 500 | 0.346 Pa
| 193066 | 450.0 CMH | 200 mmx200 mm | 3.1 m/s | 5.872 Pa | 903 | 0.624 Pa
| 194910 | 450.0 CMH | 200 mmx200 mm | 3.1 m/s | 5.872 Pa | 1500 | 1.037 Pa
95 | 189734 | 550.0 CMH | 200 mmx200 mm | 3.8 m/s | 8.772 Pa | 953 | 0.946 Pa | 3.428 Pa
| 190372 | 550.0 CMH | 200 mmx200 mm | 3.8 m/s | 8.772 Pa | 1061 | 1.054 Pa
| 195334 | 550.0 CMH | 200 mmx200 mm | 3.8 m/s | 8.772 Pa | 1000 | 0.994 Pa
| 195496 | 550.0 CMH | 200 mmx200 mm | 3.8 m/s | 8.772 Pa | 437 | 0.434 Pa
96 | 191078 | 650.0 CMH | 200 mmx200 mm | 4.5 m/s | 12.252 Pa | 500 | 0.673 Pa | 1.143 Pa
| 195496 | 650.0 CMH | 200 mmx200 mm | 4.5 m/s | 12.252 Pa | 349 | 0.470 Pa
97 | 194742 | 650.0 CMH | 200 mmx200 mm | 4.5 m/s | 12.252 Pa | 434 | 0.584 Pa | 0.584 Pa
99 | 190248 | 650.0 CMH | 200 mmx200 mm | 4.5 m/s | 12.252 Pa | 964 | 1.298 Pa | 2.135 Pa
| 193828 | 650.0 CMH | 200 mmx200 mm | 4.5 m/s | 12.252 Pa | 621 | 0.837 Pa
100 | 2177495 | 650.0 CMH | 200 mmx200 mm | 4.5 m/s | 12.252 Pa | 22 | 0.030 Pa | 0.030 Pa
101 | 162544 | 266.6 CMH | 250 mmø | 1.5 m/s | 1.369 Pa | 186 | 0.026 Pa | 0.049 Pa
| 162739 | 266.6 CMH | 250 mmø | 1.5 m/s | 1.369 Pa | 160 | 0.023 Pa
102 | 160054 | 533.2 CMH | 250 mmø | 3.0 m/s | 5.474 Pa | 147 | 0.072 Pa | 2.863 Pa
| 162049 | 533.2 CMH | 250 mmø | 3.0 m/s | 5.474 Pa | 5282 | 2.593 Pa
| 162310 | 533.2 CMH | 250 mmø | 3.0 m/s | 5.474 Pa | 403 | 0.198 Pa
103 | 160090 | 799.8 CMH | 250 mmø | 4.5 m/s | 12.317 Pa | 207 | 0.211 Pa | 0.703 Pa
| 161539 | 799.8 CMH | 250 mmø | 4.5 m/s | 12.317 Pa | 480 | 0.492 Pa
104 | 160153 | 799.8 CMH | 200 mmø | 7.1 m/s | 30.072 Pa | 194 | 0.595 Pa | 0.595 Pa
106 | 194488 | 799.8 CMH | 300 mmx300 mm | 2.5 m/s | 3.664 Pa | 117 | 0.032 Pa | 0.032 Pa
107 | 190160 | 1449.8 CMH | 300 mmx300 mm | 4.5 m/s | 12.040 Pa | 334 | 0.266 Pa | 12.609 Pa
| 190666 | 1449.8 CMH | 300 mmx300 mm | 4.5 m/s | 12.040 Pa | 117 | 0.093 Pa
| 190940 | 1449.8 CMH | 300 mmx300 mm | 4.5 m/s | 12.040 Pa | 1500 | 1.197 Pa
| 191198 | 1449.8 CMH | 300 mmx300 mm | 4.5 m/s | 12.040 Pa | 1500 | 1.197 Pa
| 191476 | 1449.8 CMH | 300 mmx300 mm | 4.5 m/s | 12.040 Pa | 1500 | 1.197 Pa
| 191522 | 1449.8 CMH | 300 mmx300 mm | 4.5 m/s | 12.040 Pa | 1500 | 1.197 Pa
| 191536 | 1449.8 CMH | 300 mmx300 mm | 4.5 m/s | 12.040 Pa | 731 | 0.583 Pa
| 192074 | 1449.8 CMH | 300 mmx300 mm | 4.5 m/s | 12.040 Pa | 1500 | 1.197 Pa
| 193426 | 1449.8 CMH | 300 mmx300 mm | 4.5 m/s | 12.040 Pa | 1500 | 1.197 Pa
| 193446 | 1449.8 CMH | 300 mmx300 mm | 4.5 m/s | 12.040 Pa | 1500 | 1.197 Pa
| 193750 | 1449.8 CMH | 300 mmx300 mm | 4.5 m/s | 12.040 Pa | 1500 | 1.197 Pa
| 194488 | 1449.8 CMH | 300 mmx300 mm | 4.5 m/s | 12.040 Pa | 1154 | 0.921 Pa
| 195040 | 1449.8 CMH | 300 mmx300 mm | 4.5 m/s | 12.040 Pa | 1463 | 1.168 Pa
108 | 189428 | 1449.8 CMH | 400 mmx400 mm | 3.5 m/s | 7.248 Pa | 0 | 0.527 Pa | 0.527 Pa
109 | 189428 | 1999.8 CMH | 400 mmx400 mm | 3.5 m/s | 7.248 Pa | 1500 | 0.000 Pa | 0.419 Pa
| 194134 | 1999.8 CMH | 400 mmx400 mm | 3.5 m/s | 7.248 Pa | 1191 | 0.419 Pa
110 | 193674 | 2249.8 CMH | 400 mmx400 mm | 3.9 m/s | 9.174 Pa | 1378 | 0.599 Pa | 2.673 Pa
| 194088 | 2249.8 CMH | 400 mmx400 mm | 3.9 m/s | 9.174 Pa | 744 | 0.324 Pa
| 194134 | 2249.8 CMH | 400 mmx400 mm | 3.9 m/s | 9.174 Pa | 309 | 0.134 Pa
| 194446 | 2249.8 CMH | 400 mmx400 mm | 3.9 m/s | 9.174 Pa | 714 | 0.311 Pa
| 195058 | 2249.8 CMH | 400 mmx400 mm | 3.9 m/s | 9.174 Pa | 1500 | 0.653 Pa
| 195374 | 2249.8 CMH | 400 mmx400 mm | 3.9 m/s | 9.174 Pa | 1500 | 0.653 Pa
112 | 160531 | 200.0 CMH | 160 mmø | 2.8 m/s | 4.591 Pa | 4028 | 2.948 Pa | 3.416 Pa
| 161389 | 200.0 CMH | 160 mmø | 2.8 m/s | 4.591 Pa | 264 | 0.193 Pa
| 161416 | 200.0 CMH | 160 mmø | 2.8 m/s | 4.591 Pa | 236 | 0.173 Pa
| 161428 | 200.0 CMH | 160 mmø | 2.8 m/s | 4.591 Pa | 139 | 0.102 Pa
114 | 1784879 | 150.0 CMH | 160 mmø | 2.1 m/s | 2.582 Pa | 368 | 0.161 Pa | 0.744 Pa
| 1784881 | 150.0 CMH | 160 mmø | 2.1 m/s | 2.582 Pa | 279 | 0.122 Pa
| 1784885 | 150.0 CMH | 160 mmø | 2.1 m/s | 2.582 Pa | 73 | 0.032 Pa
| 1784893 | 150.0 CMH | 160 mmø | 2.1 m/s | 2.582 Pa | 614 | 0.268 Pa
| 1784992 | 150.0 CMH | 160 mm | 2.1 m/s | 2.582 Pa | 369 | 0.161 Pa
115 | 160885 | 250.0 CMH | 250 mmø | 1.4 m/s | 1.203 Pa | 232 | 0.029 Pa | 0.212 Pa
| 161908 | 250.0 CMH | 250 mmø | 1.4 m/s | 1.203 Pa | 458 | 0.058 Pa
| 162664 | 250.0 CMH | 250 mmø | 1.4 m/s | 1.203 Pa | 982 | 0.124 Pa
116 | 161887 | 266.6 CMH | 250 mmø | 1.5 m/s | 1.369 Pa | 164 | 0.023 Pa | 0.074 Pa
| 163015 | 266.6 CMH | 250 mmø | 1.5 m/s | 1.369 Pa | 354 | 0.050 Pa
117 | 161329 | 266.6 CMH | 250 mmø | 1.5 m/s | 1.369 Pa | 186 | 0.026 Pa | 0.870 Pa
| 161680 | 266.6 CMH | 250 mmø | 1.5 m/s | 1.369 Pa | 5230 | 0.742 Pa
| 162673 | 266.6 CMH | 250 mmø | 1.5 m/s | 1.369 Pa | 715 | 0.101 Pa
118 | 156646 | 150.0 CMH | 160 mmø | 2.1 m/s | 2.582 Pa | 182 | 0.079 Pa | 1.572 Pa
| 159517 | 150.0 CMH | 160 mmø | 2.1 m/s | 2.582 Pa | 162 | 0.071 Pa
| 159739 | 150.0 CMH | 160 mmø | 2.1 m/s | 2.582 Pa | 238 | 0.104 Pa
| 2216972 | 150.0 CMH | 160 mmø | 2.1 m/s | 2.582 Pa | 3018 | 1.318 Pa
119 | 156322 | 300.0 CMH | 160 mmø | 4.1 m/s | 10.329 Pa | 900 | 1.371 Pa | 5.545 Pa
| 156583 | 300.0 CMH | 160 mmø | 4.1 m/s | 10.329 Pa | 619 | 0.942 Pa
| 157708 | 300.0 CMH | 160 mmø | 4.1 m/s | 10.329 Pa | 1280 | 1.950 Pa
| 158644 | 300.0 CMH | 160 mmø | 4.1 m/s | 10.329 Pa | 200 | 0.304 Pa
| 158665 | 300.0 CMH | 160 mmø | 4.1 m/s | 10.329 Pa | 34 | 0.052 Pa
| 158884 | 300.0 CMH | 160 mmø | 4.1 m/s | 10.329 Pa | 608 | 0.926 Pa
120 | 2216622 | 300.0 CMH | 200 mmø | 2.7 m/s | 4.231 Pa | 7201 | 3.705 Pa | 3.914 Pa
| 2631033 | 300.0 CMH | 200 mmø | 2.7 m/s | 4.231 Pa | 208 | 0.107 Pa
| 2631034 | 300.0 CMH | 200 mmø | 2.7 m/s | 4.231 Pa | 199 | 0.102 Pa
121 | 189728 | 300.0 CMH | 300 mmx200 mm | 1.4 m/s | 1.160 Pa | 1291 | 0.166 Pa | 0.166 Pa
122 | 189728 | 800.0 CMH | 300 mmx200 mm | 3.7 m/s | 8.248 Pa | 125 | 0.094 Pa | 0.430 Pa
| 192872 | 800.0 CMH | 300 mmx200 mm | 3.7 m/s | 8.248 Pa | 229 | 0.172 Pa
| 194570 | 800.0 CMH | 300 mmx200 mm | 3.7 m/s | 8.248 Pa | 221 | 0.165 Pa
124 | 191012 | 800.0 CMH | 350 mmx200 mm | 3.2 m/s | 6.060 Pa | 112 | 0.059 Pa | 0.176 Pa
| 191900 | 800.0 CMH | 350 mmx200 mm | 3.2 m/s | 6.060 Pa | 35 | 0.018 Pa
| 194868 | 800.0 CMH | 350 mmx200 mm | 3.2 m/s | 6.060 Pa | 188 | 0.099 Pa
125 | 189886 | 1100.0 CMH | 350 mmx200 mm | 4.4 m/s | 11.457 Pa | 1000 | 0.937 Pa | 9.368 Pa
| 190540 | 1100.0 CMH | 350 mmx200 mm | 4.4 m/s | 11.457 Pa | 1500 | 1.405 Pa
| 190586 | 1100.0 CMH | 350 mmx200 mm | 4.4 m/s | 11.457 Pa | 1500 | 1.405 Pa
| 191062 | 1100.0 CMH | 350 mmx200 mm | 4.4 m/s | 11.457 Pa | 1500 | 1.405 Pa
| 191190 | 1100.0 CMH | 350 mmx200 mm | 4.4 m/s | 11.457 Pa | 1500 | 1.405 Pa
| 192052 | 1100.0 CMH | 350 mmx200 mm | 4.4 m/s | 11.457 Pa | 1500 | 1.405 Pa
| 194732 | 1100.0 CMH | 350 mmx200 mm | 4.4 m/s | 11.457 Pa | 188 | 0.176 Pa
| 194868 | 1100.0 CMH | 350 mmx200 mm | 4.4 m/s | 11.457 Pa | 1312 | 1.229 Pa
126 | 190194 | 1100.0 CMH | 350 mmx200 mm | 4.4 m/s | 11.457 Pa | 133 | 0.125 Pa | 1.624 Pa
| 190702 | 1100.0 CMH | 350 mmx200 mm | 4.4 m/s | 11.457 Pa | 600 | 0.562 Pa
| 192616 | 1100.0 CMH | 350 mmx200 mm | 4.4 m/s | 11.457 Pa | 1000 | 0.937 Pa
128 | 190088 | 1100.0 CMH | 350 mmx200 mm | 4.4 m/s | 11.457 Pa | 800 | 0.749 Pa | 2.466 Pa
| 192750 | 1100.0 CMH | 350 mmx200 mm | 4.4 m/s | 11.457 Pa | 1004 | 0.940 Pa
| 195508 | 1100.0 CMH | 350 mmx200 mm | 4.4 m/s | 11.457 Pa | 828 | 0.776 Pa
129 | 189592 | 1100.0 CMH | 350 mmx250 mm | 3.5 m/s | 7.333 Pa | 374 | 0.197 Pa | 0.197 Pa
130 | 190744 | 1100.0 CMH | 400 mmx300 mm | 2.5 m/s | 3.899 Pa | 493 | 0.120 Pa | 0.120 Pa
131 | 190136 | 1600.0 CMH | 400 mmx300 mm | 3.7 m/s | 8.248 Pa | 350 | 0.168 Pa | 1.924 Pa
| 190480 | 1600.0 CMH | 400 mmx300 mm | 3.7 m/s | 8.248 Pa | 476 | 0.228 Pa
| 190744 | 1600.0 CMH | 400 mmx300 mm | 3.7 m/s | 8.248 Pa | 796 | 0.381 Pa
| 191736 | 1600.0 CMH | 400 mmx300 mm | 3.7 m/s | 8.248 Pa | 350 | 0.168 Pa
| 193270 | 1600.0 CMH | 400 mmx300 mm | 3.7 m/s | 8.248 Pa | 1300 | 0.623 Pa
| 194140 | 1600.0 CMH | 400 mmx300 mm | 3.7 m/s | 8.248 Pa | 703 | 0.337 Pa
| 195022 | 1600.0 CMH | 400 mmx300 mm | 3.7 m/s | 8.248 Pa | 41 | 0.019 Pa
132 | 194072 | 1600.0 CMH | 350 mmx350 mm | 3.6 m/s | 7.915 Pa | 826 | 0.371 Pa | 0.585 Pa
| 195152 | 1600.0 CMH | 350 mmx350 mm | 3.6 m/s | 7.915 Pa | 475 | 0.214 Pa
133 | 189978 | 1600.0 CMH | 350 mmx350 mm | 3.6 m/s | 7.915 Pa | 1300 | 0.585 Pa | 0.704 Pa
| 190388 | 1600.0 CMH | 350 mmx350 mm | 3.6 m/s | 7.915 Pa | 265 | 0.119 Pa
134 | 190810 | 1600.0 CMH | 500 mmx500 mm | 1.8 m/s | 1.900 Pa | 680 | 0.054 Pa | 0.150 Pa
| 193640 | 1600.0 CMH | 500 mmx500 mm | 1.8 m/s | 1.900 Pa | 1200 | 0.096 Pa
135 | 172957 | 150.0 CMH | 160 mmø | 2.1 m/s | 2.582 Pa | 168 | 0.073 Pa | 1.365 Pa
| 173098 | 150.0 CMH | 160 mmø | 2.1 m/s | 2.582 Pa | 270 | 0.118 Pa
| 173272 | 150.0 CMH | 160 mmø | 2.1 m/s | 2.582 Pa | 574 | 0.251 Pa
| 174691 | 150.0 CMH | 160 mmø | 2.1 m/s | 2.582 Pa | 198 | 0.086 Pa
| 2213465 | 150.0 CMH | 160 mmø | 2.1 m/s | 2.582 Pa | 1916 | 0.837 Pa
136 | 173593 | 250.0 CMH | 160 mmø | 3.5 m/s | 7.173 Pa | 100 | 0.109 Pa | 1.195 Pa
| 2215601 | 250.0 CMH | 160 mmø | 3.5 m/s | 7.173 Pa | 992 | 1.086 Pa
137 | 189408 | 250.0 CMH | 200 mmx200 mm | 1.7 m/s | 1.812 Pa | 41 | 0.010 Pa | 0.093 Pa
| 189936 | 250.0 CMH | 200 mmx200 mm | 1.7 m/s | 1.812 Pa | 344 | 0.083 Pa
138 | 156994 | 100.0 CMH | 160 mmø | 1.4 m/s | 1.148 Pa | 305 | 0.065 Pa | 0.307 Pa
| 157825 | 100.0 CMH | 160 mmø | 1.4 m/s | 1.148 Pa | 637 | 0.135 Pa
| 157981 | 100.0 CMH | 160 mmø | 1.4 m/s | 1.148 Pa | 217 | 0.046 Pa
| 567516 | 100.0 CMH | 160 mm | 1.4 m/s | 1.148 Pa | 293 | 0.062 Pa
139 | 190436 | 300.0 CMH | 200 mmx200 mm | 2.1 m/s | 2.610 Pa | 902 | 0.301 Pa | 1.151 Pa
| 190730 | 300.0 CMH | 200 mmx200 mm | 2.1 m/s | 2.610 Pa | 1048 | 0.349 Pa
| 191552 | 300.0 CMH | 200 mmx200 mm | 2.1 m/s | 2.610 Pa | 1500 | 0.500 Pa
140 | 190550 | 400.0 CMH | 200 mmx200 mm | 2.8 m/s | 4.640 Pa | 1000 | 0.559 Pa | 1.928 Pa
| 190730 | 400.0 CMH | 200 mmx200 mm | 2.8 m/s | 4.640 Pa | 952 | 0.532 Pa
| 192866 | 400.0 CMH | 200 mmx200 mm | 2.8 m/s | 4.640 Pa | 437 | 0.244 Pa
| 193382 | 400.0 CMH | 200 mmx200 mm | 2.8 m/s | 4.640 Pa | 1061 | 0.593 Pa
141 | 191042 | 500.0 CMH | 200 mmx200 mm | 3.5 m/s | 7.250 Pa | 709 | 0.593 Pa | 0.885 Pa
| 192866 | 500.0 CMH | 200 mmx200 mm | 3.5 m/s | 7.250 Pa | 349 | 0.292 Pa
142 | 1588941 | 500.0 CMH | 200 mmx200 mm | 3.5 m/s | 7.250 Pa | 304 | 0.255 Pa | 0.255 Pa
145 | 194788 | 500.0 CMH | 200 mmx200 mm | 3.5 m/s | 7.250 Pa | 69 | 0.058 Pa | 0.058 Pa
146 | 157108 | 100.0 CMH | 160 mmø | 1.4 m/s | 1.148 Pa | 305 | 0.065 Pa | 0.308 Pa
| 157945 | 100.0 CMH | 160 mmø | 1.4 m/s | 1.148 Pa | 637 | 0.135 Pa
| 159301 | 100.0 CMH | 160 mmø | 1.4 m/s | 1.148 Pa | 217 | 0.046 Pa
| 461452 | 100.0 CMH | 160 mm | 1.4 m/s | 1.148 Pa | 294 | 0.062 Pa
147 | 189836 | 200.0 CMH | 200 mmx200 mm | 1.4 m/s | 1.160 Pa | 1250 | 0.202 Pa | 0.559 Pa
| 189870 | 200.0 CMH | 200 mmx200 mm | 1.4 m/s | 1.160 Pa | 697 | 0.113 Pa
| 190230 | 200.0 CMH | 200 mmx200 mm | 1.4 m/s | 1.160 Pa | 156 | 0.025 Pa
| 190436 | 200.0 CMH | 200 mmx200 mm | 1.4 m/s | 1.160 Pa | 598 | 0.097 Pa
| 193368 | 200.0 CMH | 200 mmx200 mm | 1.4 m/s | 1.160 Pa | 750 | 0.121 Pa
148 | 156277 | 100.0 CMH | 160 mmø | 1.4 m/s | 1.148 Pa | 100 | 0.021 Pa | 0.330 Pa
| 156988 | 100.0 CMH | 160 mmø | 1.4 m/s | 1.148 Pa | 423 | 0.090 Pa
| 159085 | 100.0 CMH | 160 mmø | 1.4 m/s | 1.148 Pa | 207 | 0.044 Pa
| 159406 | 100.0 CMH | 160 mmø | 1.4 m/s | 1.148 Pa | 305 | 0.065 Pa
| 567514 | 100.0 CMH | 160 mm | 1.4 m/s | 1.148 Pa | 241 | 0.051 Pa
| 1268829 | 100.0 CMH | 160 mmø | 1.4 m/s | 1.148 Pa | 282 | 0.060 Pa
149 | 190230 | 100.0 CMH | 200 mmx200 mm | 0.7 m/s | 0.290 Pa | 344 | 0.016 Pa | 0.018 Pa
| 190258 | 100.0 CMH | 200 mmx200 mm | 0.7 m/s | 0.290 Pa | 38 | 0.002 Pa
150 | 1746749 | 300.0 CMH | 200 mm | 2.7 m/s | 4.231 Pa | 493 | 0.253 Pa | 0.253 Pa
151 | 172891 | 600.0 CMH | 250 mmø | 3.4 m/s | 6.932 Pa | 286 | 0.174 Pa | 1.028 Pa
| 172906 | 600.0 CMH | 250 mmø | 3.4 m/s | 6.932 Pa | 833 | 0.506 Pa
| 174103 | 600.0 CMH | 250 mmø | 3.4 m/s | 6.932 Pa | 312 | 0.190 Pa
| 2261372 | 600.0 CMH | 250 mmø | 3.4 m/s | 6.932 Pa | 262 | 0.159 Pa
152 | 172918 | 950.0 CMH | 280 mmø | 4.3 m/s | 11.044 Pa | 210 | 0.169 Pa | 0.539 Pa
| 173080 | 950.0 CMH | 280 mmø | 4.3 m/s | 11.044 Pa | 435 | 0.350 Pa
| 173758 | 950.0 CMH | 280 mmø | 4.3 m/s | 11.044 Pa | 25 | 0.020 Pa
153 | 175513 | 1150.0 CMH | 280 mmø | 5.2 m/s | 16.184 Pa | 3361 | 3.830 Pa | 7.451 Pa
| 176080 | 1150.0 CMH | 280 mmø | 5.2 m/s | 16.184 Pa | 3177 | 3.621 Pa
154 | 173443 | 1300.0 CMH | 280 mmø | 5.9 m/s | 20.681 Pa | 5914 | 8.437 Pa | 20.735 Pa
| 174085 | 1300.0 CMH | 280 mmø | 5.9 m/s | 20.681 Pa | 127 | 0.181 Pa
| 174235 | 1300.0 CMH | 280 mmø | 5.9 m/s | 20.681 Pa | 1893 | 2.700 Pa
| 174301 | 1300.0 CMH | 280 mmø | 5.9 m/s | 20.681 Pa | 6000 | 8.560 Pa
| 174409 | 1300.0 CMH | 280 mmø | 5.9 m/s | 20.681 Pa | 216 | 0.308 Pa
| 175249 | 1300.0 CMH | 280 mmø | 5.9 m/s | 20.681 Pa | 385 | 0.549 Pa
155 | 1746752 | 300.0 CMH | 200 mm | 2.7 m/s | 4.231 Pa | 487 | 0.251 Pa | 0.251 Pa
156 | 173575 | 250.0 CMH | 250 mmø | 1.4 m/s | 1.203 Pa | 2555 | 0.323 Pa | 0.323 Pa
157 | 173074 | 500.0 CMH | 250 mmø | 2.8 m/s | 4.814 Pa | 641 | 0.280 Pa | 3.783 Pa
| 173332 | 500.0 CMH | 250 mmø | 2.8 m/s | 4.814 Pa | 391 | 0.171 Pa
| 173425 | 500.0 CMH | 250 mmø | 2.8 m/s | 4.814 Pa | 2500 | 1.093 Pa
| 173914 | 500.0 CMH | 250 mmø | 2.8 m/s | 4.814 Pa | 250 | 0.109 Pa
| 175060 | 500.0 CMH | 250 mmø | 2.8 m/s | 4.814 Pa | 3132 | 1.369 Pa
| 175165 | 500.0 CMH | 250 mmø | 2.8 m/s | 4.814 Pa | 277 | 0.121 Pa
| 175540 | 500.0 CMH | 250 mmø | 2.8 m/s | 4.814 Pa | 131 | 0.057 Pa
| 175951 | 500.0 CMH | 250 mmø | 2.8 m/s | 4.814 Pa | 923 | 0.403 Pa
| 2177368 | 500.0 CMH | 250 mmø | 2.8 m/s | 4.814 Pa | 89 | 0.039 Pa
| 2213549 | 500.0 CMH | 250 mmø | 2.8 m/s | 4.814 Pa | 320 | 0.140 Pa
159 | 175813 | 125.0 CMH | 160 mmø | 1.7 m/s | 1.793 Pa | 3160 | 0.996 Pa | 1.113 Pa
| 2640740 | 125.0 CMH | 160 mm | 1.7 m/s | 1.793 Pa | 369 | 0.116 Pa
160 | 174175 | 250.0 CMH | 160 mmø | 3.5 m/s | 7.173 Pa | 282 | 0.308 Pa | 4.662 Pa
| 174277 | 250.0 CMH | 160 mmø | 3.5 m/s | 7.173 Pa | 2691 | 2.945 Pa
| 175693 | 250.0 CMH | 160 mmø | 3.5 m/s | 7.173 Pa | 347 | 0.380 Pa
| 1722583 | 250.0 CMH | 160 mmø | 3.5 m/s | 7.173 Pa | 939 | 1.028 Pa
161 | 2214634 | 250.0 CMH | 250 mmø | 1.4 m/s | 1.203 Pa | 135 | 0.017 Pa | 0.017 Pa
162 | 2640737 | 125.0 CMH | 160 mm | 1.7 m/s | 1.793 Pa | 401 | 0.127 Pa | 0.127 Pa
163 | 1784933 | 100.0 CMH | 160 mmø | 1.4 m/s | 1.148 Pa | 368 | 0.078 Pa | 0.359 Pa
| 1784935 | 100.0 CMH | 160 mmø | 1.4 m/s | 1.148 Pa | 279 | 0.059 Pa
| 1784939 | 100.0 CMH | 160 mmø | 1.4 m/s | 1.148 Pa | 73 | 0.015 Pa
| 1784947 | 100.0 CMH | 160 mmø | 1.4 m/s | 1.148 Pa | 614 | 0.130 Pa
| 1803421 | 100.0 CMH | 160 mm | 1.4 m/s | 1.148 Pa | 361 | 0.076 Pa
164 | 160369 | 150.0 CMH | 160 mmø | 2.1 m/s | 2.582 Pa | 38 | 0.017 Pa | 0.661 Pa
| 160819 | 150.0 CMH | 160 mmø | 2.1 m/s | 2.582 Pa | 320 | 0.140 Pa
| 162067 | 150.0 CMH | 160 mmø | 2.1 m/s | 2.582 Pa | 248 | 0.108 Pa
| 163234 | 150.0 CMH | 160 mmø | 2.1 m/s | 2.582 Pa | 614 | 0.268 Pa
| 1803474 | 150.0 CMH | 160 mm | 2.1 m/s | 2.582 Pa | 293 | 0.128 Pa
165 | 160687 | 150.0 CMH | 160 mmø | 2.1 m/s | 2.582 Pa | 248 | 0.108 Pa | 0.516 Pa
| 162079 | 150.0 CMH | 160 mmø | 2.1 m/s | 2.582 Pa | 141 | 0.062 Pa
| 163186 | 150.0 CMH | 160 mmø | 2.1 m/s | 2.582 Pa | 309 | 0.135 Pa
| 163378 | 150.0 CMH | 160 mmø | 2.1 m/s | 2.582 Pa | 132 | 0.058 Pa
| 1803488 | 150.0 CMH | 160 mm | 2.1 m/s | 2.582 Pa | 352 | 0.154 Pa
166 | 160126 | 100.0 CMH | 160 mmø | 1.4 m/s | 1.148 Pa | 368 | 0.078 Pa | 0.360 Pa
| 160150 | 100.0 CMH | 160 mmø | 1.4 m/s | 1.148 Pa | 279 | 0.059 Pa
| 161521 | 100.0 CMH | 160 mmø | 1.4 m/s | 1.148 Pa | 73 | 0.015 Pa
| 163057 | 100.0 CMH | 160 mmø | 1.4 m/s | 1.148 Pa | 614 | 0.130 Pa
| 1784775 | 100.0 CMH | 160 mm | 1.4 m/s | 1.148 Pa | 363 | 0.077 Pa
167 | 156394 | 125.0 CMH | 160 mmø | 1.7 m/s | 1.793 Pa | 103 | 0.032 Pa | 0.560 Pa
| 156823 | 125.0 CMH | 160 mmø | 1.7 m/s | 1.793 Pa | 1367 | 0.431 Pa
| 158188 | 125.0 CMH | 160 mmø | 1.7 m/s | 1.793 Pa | 49 | 0.016 Pa
| 158194 | 125.0 CMH | 160 mmø | 1.7 m/s | 1.793 Pa | 256 | 0.081 Pa
168 | 156883 | 250.0 CMH | 160 mmø | 3.5 m/s | 7.173 Pa | 129 | 0.141 Pa | 0.454 Pa
| 157471 | 250.0 CMH | 160 mmø | 3.5 m/s | 7.173 Pa | 114 | 0.125 Pa
| 157531 | 250.0 CMH | 160 mmø | 3.5 m/s | 7.173 Pa | 53 | 0.058 Pa
| 159250 | 250.0 CMH | 160 mmø | 3.5 m/s | 7.173 Pa | 118 | 0.129 Pa
169 | 2235285 | 250.0 CMH | 280 mmø | 1.1 m/s | 0.765 Pa | 282 | 0.021 Pa | 0.021 Pa
170 | 160201 | 150.0 CMH | 160 mmø | 2.1 m/s | 2.582 Pa | 574 | 0.251 Pa | 1.340 Pa
| 161086 | 150.0 CMH | 160 mmø | 2.1 m/s | 2.582 Pa | 232 | 0.101 Pa
| 161776 | 150.0 CMH | 160 mmø | 2.1 m/s | 2.582 Pa | 236 | 0.103 Pa
| 162565 | 150.0 CMH | 160 mmø | 2.1 m/s | 2.582 Pa | 110 | 0.048 Pa
| 2215833 | 150.0 CMH | 160 mmø | 2.1 m/s | 2.582 Pa | 1916 | 0.837 Pa
171 | 161341 | 250.0 CMH | 160 mmø | 3.5 m/s | 7.173 Pa | 100 | 0.109 Pa | 1.195 Pa
| 2216005 | 250.0 CMH | 160 mmø | 3.5 m/s | 7.173 Pa | 992 | 1.086 Pa
172 | 190200 | 250.0 CMH | 200 mmx200 mm | 1.7 m/s | 1.812 Pa | 344 | 0.083 Pa | 0.093 Pa
| 190272 | 250.0 CMH | 200 mmx200 mm | 1.7 m/s | 1.812 Pa | 41 | 0.010 Pa
173 | 189894 | 350.0 CMH | 200 mmx200 mm | 2.4 m/s | 3.552 Pa | 750 | 0.330 Pa | 1.517 Pa
| 190200 | 350.0 CMH | 200 mmx200 mm | 2.4 m/s | 3.552 Pa | 156 | 0.069 Pa
| 191278 | 350.0 CMH | 200 mmx200 mm | 2.4 m/s | 3.552 Pa | 1000 | 0.440 Pa
| 191402 | 350.0 CMH | 200 mmx200 mm | 2.4 m/s | 3.552 Pa | 697 | 0.306 Pa
| 192948 | 350.0 CMH | 200 mmx200 mm | 2.4 m/s | 3.552 Pa | 598 | 0.263 Pa
| 195398 | 350.0 CMH | 200 mmx200 mm | 2.4 m/s | 3.552 Pa | 250 | 0.110 Pa
174 | 191982 | 450.0 CMH | 200 mmx200 mm | 3.1 m/s | 5.872 Pa | 1500 | 1.037 Pa | 2.384 Pa
| 192030 | 450.0 CMH | 200 mmx200 mm | 3.1 m/s | 5.872 Pa | 548 | 0.378 Pa
| 192948 | 450.0 CMH | 200 mmx200 mm | 3.1 m/s | 5.872 Pa | 902 | 0.624 Pa
| 194714 | 450.0 CMH | 200 mmx200 mm | 3.1 m/s | 5.872 Pa | 500 | 0.346 Pa
175 | 189490 | 550.0 CMH | 200 mmx200 mm | 3.8 m/s | 8.772 Pa | 437 | 0.434 Pa | 3.428 Pa
| 191584 | 550.0 CMH | 200 mmx200 mm | 3.8 m/s | 8.772 Pa | 1061 | 1.054 Pa
| 192030 | 550.0 CMH | 200 mmx200 mm | 3.8 m/s | 8.772 Pa | 952 | 0.946 Pa
| 192354 | 550.0 CMH | 200 mmx200 mm | 3.8 m/s | 8.772 Pa | 1000 | 0.994 Pa
176 | 189490 | 650.0 CMH | 200 mmx200 mm | 4.5 m/s | 12.252 Pa | 349 | 0.470 Pa | 2.723 Pa
| 191478 | 650.0 CMH | 200 mmx200 mm | 4.5 m/s | 12.252 Pa | 418 | 0.563 Pa
| 194234 | 650.0 CMH | 200 mmx200 mm | 4.5 m/s | 12.252 Pa | 1256 | 1.691 Pa
178 | 194668 | 650.0 CMH | 200 mmx200 mm | 4.5 m/s | 12.252 Pa | 343 | 0.462 Pa | 0.462 Pa
179 | 189658 | 650.0 CMH | 200 mmx200 mm | 4.5 m/s | 12.252 Pa | 519 | 0.698 Pa | 0.865 Pa
| 1775479 | 650.0 CMH | 200 mmx200 mm | 4.5 m/s | 12.252 Pa | 124 | 0.167 Pa
180 | 160114 | 100.0 CMH | 160 mmø | 1.4 m/s | 1.148 Pa | 280 | 0.059 Pa | 0.287 Pa
| 161014 | 100.0 CMH | 160 mmø | 1.4 m/s | 1.148 Pa | 358 | 0.076 Pa
| 161704 | 100.0 CMH | 160 mmø | 1.4 m/s | 1.148 Pa | 155 | 0.033 Pa
| 161767 | 100.0 CMH | 160 mmø | 1.4 m/s | 1.148 Pa | 449 | 0.095 Pa
| 162388 | 100.0 CMH | 160 mmø | 1.4 m/s | 1.148 Pa | 114 | 0.024 Pa
181 | 160372 | 150.0 CMH | 160 mmø | 2.1 m/s | 2.582 Pa | 253 | 0.111 Pa | 1.373 Pa
| 160561 | 150.0 CMH | 160 mmø | 2.1 m/s | 2.582 Pa | 578 | 0.253 Pa
| 160804 | 150.0 CMH | 160 mmø | 2.1 m/s | 2.582 Pa | 736 | 0.322 Pa
| 161404 | 150.0 CMH | 160 mmø | 2.1 m/s | 2.582 Pa | 231 | 0.101 Pa
| 162145 | 150.0 CMH | 160 mmø | 2.1 m/s | 2.582 Pa | 146 | 0.064 Pa
| 162292 | 150.0 CMH | 160 mmø | 2.1 m/s | 2.582 Pa | 617 | 0.269 Pa
| 163012 | 150.0 CMH | 160 mmø | 2.1 m/s | 2.582 Pa | 238 | 0.104 Pa
| 1784715 | 150.0 CMH | 160 mm | 2.1 m/s | 2.582 Pa | 343 | 0.150 Pa
183 | 159952 | 250.0 CMH | 160 mmø | 3.5 m/s | 7.173 Pa | 98 | 0.108 Pa | 0.830 Pa
| 161443 | 250.0 CMH | 160 mmø | 3.5 m/s | 7.173 Pa | 660 | 0.722 Pa
184 | 160234 | 300.0 CMH | 250 mmø | 1.7 m/s | 1.733 Pa | 167 | 0.029 Pa | 0.702 Pa
| 160429 | 300.0 CMH | 250 mmø | 1.7 m/s | 1.733 Pa | 476 | 0.083 Pa
| 160516 | 300.0 CMH | 250 mmø | 1.7 m/s | 1.733 Pa | 1577 | 0.276 Pa
| 161071 | 300.0 CMH | 250 mmø | 1.7 m/s | 1.733 Pa | 83 | 0.015 Pa
| 161089 | 300.0 CMH | 250 mmø | 1.7 m/s | 1.733 Pa | 212 | 0.037 Pa
| 161332 | 300.0 CMH | 250 mmø | 1.7 m/s | 1.733 Pa | 280 | 0.049 Pa
| 161542 | 300.0 CMH | 250 mmø | 1.7 m/s | 1.733 Pa | 128 | 0.022 Pa
| 162583 | 300.0 CMH | 250 mmø | 1.7 m/s | 1.733 Pa | 652 | 0.114 Pa
| 163354 | 300.0 CMH | 250 mmø | 1.7 m/s | 1.733 Pa | 245 | 0.043 Pa
| 2178095 | 300.0 CMH | 250 mmø | 1.7 m/s | 1.733 Pa | 189 | 0.033 Pa
185 | 160471 | 250.0 CMH | 250 mmø | 1.4 m/s | 1.203 Pa | 152 | 0.019 Pa | 1.078 Pa
| 160864 | 250.0 CMH | 250 mmø | 1.4 m/s | 1.203 Pa | 3157 | 0.400 Pa
| 160972 | 250.0 CMH | 250 mmø | 1.4 m/s | 1.203 Pa | 983 | 0.124 Pa
| 161758 | 250.0 CMH | 250 mmø | 1.4 m/s | 1.203 Pa | 373 | 0.047 Pa
| 162085 | 250.0 CMH | 250 mmø | 1.4 m/s | 1.203 Pa | 42 | 0.005 Pa
| 162280 | 250.0 CMH | 250 mmø | 1.4 m/s | 1.203 Pa | 2650 | 0.335 Pa
| 162343 | 250.0 CMH | 250 mmø | 1.4 m/s | 1.203 Pa | 606 | 0.077 Pa
| 162586 | 250.0 CMH | 250 mmø | 1.4 m/s | 1.203 Pa | 208 | 0.026 Pa
| 163315 | 250.0 CMH | 250 mmø | 1.4 m/s | 1.203 Pa | 186 | 0.024 Pa
| 2178043 | 250.0 CMH | 250 mmø | 1.4 m/s | 1.203 Pa | 159 | 0.020 Pa
188 | 173203 | 175.0 CMH | 160 mmø | 2.4 m/s | 3.515 Pa | 387 | 0.223 Pa | 2.805 Pa
| 175339 | 175.0 CMH | 160 mmø | 2.4 m/s | 3.515 Pa | 306 | 0.176 Pa
| 175498 | 175.0 CMH | 160 mmø | 2.4 m/s | 3.515 Pa | 4180 | 2.406 Pa
189 | 173155 | 350.0 CMH | 160 mmø | 4.8 m/s | 14.059 Pa | 348 | 0.701 Pa | 28.434 Pa
| 173506 | 350.0 CMH | 160 mmø | 4.8 m/s | 14.059 Pa | 1593 | 3.214 Pa
| 173887 | 350.0 CMH | 160 mmø | 4.8 m/s | 14.059 Pa | 3953 | 7.973 Pa
| 174844 | 350.0 CMH | 160 mmø | 4.8 m/s | 14.059 Pa | 95 | 0.193 Pa
| 174928 | 350.0 CMH | 160 mmø | 4.8 m/s | 14.059 Pa | 99 | 0.199 Pa
| 175030 | 350.0 CMH | 160 mmø | 4.8 m/s | 14.059 Pa | 1534 | 3.094 Pa
| 175453 | 350.0 CMH | 160 mmø | 4.8 m/s | 14.059 Pa | 2013 | 4.060 Pa
| 175681 | 350.0 CMH | 160 mmø | 4.8 m/s | 14.059 Pa | 4059 | 8.188 Pa
| 1746814 | 350.0 CMH | 160 mmø | 4.8 m/s | 14.059 Pa | 402 | 0.812 Pa
191 | 173842 | 175.0 CMH | 160 mmø | 2.4 m/s | 3.515 Pa | 306 | 0.176 Pa | 0.416 Pa
| 175132 | 175.0 CMH | 160 mmø | 2.4 m/s | 3.515 Pa | 417 | 0.240 Pa
192 | 160039 | 400.0 CMH | 250 mmø | 2.3 m/s | 3.081 Pa | 485 | 0.142 Pa | 0.715 Pa
| 161527 | 400.0 CMH | 250 mmø | 2.3 m/s | 3.081 Pa | 628 | 0.184 Pa
| 162958 | 400.0 CMH | 250 mmø | 2.3 m/s | 3.081 Pa | 745 | 0.218 Pa
| 163117 | 400.0 CMH | 250 mmø | 2.3 m/s | 3.081 Pa | 449 | 0.131 Pa
| 1772496 | 400.0 CMH | 250 mmø | 2.3 m/s | 3.081 Pa | 135 | 0.040 Pa
193 | 159901 | 100.0 CMH | 160 mmø | 1.4 m/s | 1.148 Pa | 637 | 0.135 Pa | 0.307 Pa
| 161494 | 100.0 CMH | 160 mmø | 1.4 m/s | 1.148 Pa | 305 | 0.065 Pa
| 163384 | 100.0 CMH | 160 mmø | 1.4 m/s | 1.148 Pa | 217 | 0.046 Pa
| 1734185 | 100.0 CMH | 160 mm | 1.4 m/s | 1.148 Pa | 290 | 0.062 Pa
194 | 160063 | 100.0 CMH | 160 mmø | 1.4 m/s | 1.148 Pa | 244 | 0.052 Pa | 0.307 Pa
| 160666 | 100.0 CMH | 160 mmø | 1.4 m/s | 1.148 Pa | 277 | 0.059 Pa
| 160930 | 100.0 CMH | 160 mmø | 1.4 m/s | 1.148 Pa | 344 | 0.073 Pa
| 161452 | 100.0 CMH | 160 mmø | 1.4 m/s | 1.148 Pa | 292 | 0.062 Pa
| 1734201 | 100.0 CMH | 160 mm | 1.4 m/s | 1.148 Pa | 290 | 0.062 Pa
195 | 160597 | 100.0 CMH | 160 mmø | 1.4 m/s | 1.148 Pa | 305 | 0.065 Pa | 0.307 Pa
| 162862 | 100.0 CMH | 160 mmø | 1.4 m/s | 1.148 Pa | 637 | 0.135 Pa
| 163426 | 100.0 CMH | 160 mmø | 1.4 m/s | 1.148 Pa | 217 | 0.046 Pa
| 1734197 | 100.0 CMH | 160 mm | 1.4 m/s | 1.148 Pa | 290 | 0.062 Pa
196 | 161263 | 100.0 CMH | 160 mmø | 1.4 m/s | 1.148 Pa | 637 | 0.135 Pa | 0.307 Pa
| 162649 | 100.0 CMH | 160 mmø | 1.4 m/s | 1.148 Pa | 217 | 0.046 Pa
| 163363 | 100.0 CMH | 160 mmø | 1.4 m/s | 1.148 Pa | 305 | 0.065 Pa
| 1734139 | 100.0 CMH | 160 mm | 1.4 m/s | 1.148 Pa | 290 | 0.062 Pa
197 | 157876 | 150.0 CMH | 160 mmø | 2.1 m/s | 2.582 Pa | 182 | 0.079 Pa | 0.267 Pa
| 159112 | 150.0 CMH | 160 mmø | 2.1 m/s | 2.582 Pa | 192 | 0.084 Pa
| 159262 | 150.0 CMH | 160 mmø | 2.1 m/s | 2.582 Pa | 238 | 0.104 Pa
198 | 159166 | 250.0 CMH | 250 mmø | 1.4 m/s | 1.203 Pa | 377 | 0.048 Pa | 0.138 Pa
| 159433 | 250.0 CMH | 250 mmø | 1.4 m/s | 1.203 Pa | 134 | 0.017 Pa
| 159448 | 250.0 CMH | 250 mmø | 1.4 m/s | 1.203 Pa | 432 | 0.055 Pa
| 2235690 | 250.0 CMH | 250 mmø | 1.4 m/s | 1.203 Pa | 145 | 0.018 Pa
199 | 2233788 | 500.0 CMH | 250 mmø | 2.8 m/s | 4.814 Pa | 210 | 0.092 Pa | 0.092 Pa
200 | 172882 | 200.0 CMH | 160 mmø | 2.8 m/s | 4.591 Pa | 304 | 0.222 Pa | 12.166 Pa
| 173200 | 200.0 CMH | 160 mmø | 2.8 m/s | 4.591 Pa | 383 | 0.280 Pa
| 173248 | 200.0 CMH | 160 mmø | 2.8 m/s | 4.591 Pa | 1117 | 0.817 Pa
| 173461 | 200.0 CMH | 160 mmø | 2.8 m/s | 4.591 Pa | 145 | 0.106 Pa
| 174271 | 200.0 CMH | 160 mmø | 2.8 m/s | 4.591 Pa | 3072 | 2.248 Pa
| 174616 | 200.0 CMH | 160 mmø | 2.8 m/s | 4.591 Pa | 332 | 0.243 Pa
| 175174 | 200.0 CMH | 160 mmø | 2.8 m/s | 4.591 Pa | 6000 | 4.391 Pa
| 175735 | 200.0 CMH | 160 mmø | 2.8 m/s | 4.591 Pa | 1884 | 1.378 Pa
| 175810 | 200.0 CMH | 160 mmø | 2.8 m/s | 4.591 Pa | 2629 | 1.924 Pa
| 176110 | 200.0 CMH | 160 mmø | 2.8 m/s | 4.591 Pa | 383 | 0.280 Pa
| 176152 | 200.0 CMH | 160 mmø | 2.8 m/s | 4.591 Pa | 377 | 0.276 Pa
201 | 158521 | 250.0 CMH | 250 mmø | 1.4 m/s | 1.203 Pa | 507 | 0.064 Pa | 0.868 Pa
| 1565151 | 250.0 CMH | 250 mm | 1.4 m/s | 1.203 Pa | 331 | 0.042 Pa
| 2235693 | 250.0 CMH | 250 mmø | 1.4 m/s | 1.203 Pa | 6022 | 0.762 Pa
202 | 157273 | 125.0 CMH | 160 mmø | 1.7 m/s | 1.793 Pa | 33 | 0.010 Pa | 0.133 Pa
| 158074 | 125.0 CMH | 160 mmø | 1.7 m/s | 1.793 Pa | 103 | 0.032 Pa
| 159454 | 125.0 CMH | 160 mmø | 1.7 m/s | 1.793 Pa | 286 | 0.090 Pa
203 | 157342 | 350.0 CMH | 200 mmø | 3.1 m/s | 5.759 Pa | 677 | 0.460 Pa | 0.666 Pa
| 159874 | 350.0 CMH | 200 mmø | 3.1 m/s | 5.759 Pa | 303 | 0.206 Pa
204 | 159475 | 350.0 CMH | 160 mmø | 4.8 m/s | 14.059 Pa | 840 | 1.695 Pa | 2.912 Pa
| 2175311 | 350.0 CMH | 160 mmø | 4.8 m/s | 14.059 Pa | 109 | 0.219 Pa
| 2175323 | 350.0 CMH | 160 mmø | 4.8 m/s | 14.059 Pa | 495 | 0.998 Pa
205 | 156700 | 100.0 CMH | 160 mmø | 1.4 m/s | 1.148 Pa | 277 | 0.059 Pa | 0.307 Pa
| 159052 | 100.0 CMH | 160 mmø | 1.4 m/s | 1.148 Pa | 600 | 0.127 Pa
| 159337 | 100.0 CMH | 160 mmø | 1.4 m/s | 1.148 Pa | 244 | 0.052 Pa
| 1565219 | 100.0 CMH | 160 mm | 1.4 m/s | 1.148 Pa | 328 | 0.070 Pa
206 | 173317 | 150.0 CMH | 160 mmø | 2.1 m/s | 2.582 Pa | 136 | 0.059 Pa | 1.204 Pa
| 173632 | 150.0 CMH | 160 mmø | 2.1 m/s | 2.582 Pa | 238 | 0.104 Pa
| 173671 | 150.0 CMH | 160 mmø | 2.1 m/s | 2.582 Pa | 702 | 0.307 Pa
| 175066 | 150.0 CMH | 160 mmø | 2.1 m/s | 2.582 Pa | 231 | 0.101 Pa
| 175243 | 150.0 CMH | 160 mmø | 2.1 m/s | 2.582 Pa | 578 | 0.253 Pa
| 175867 | 150.0 CMH | 160 mmø | 2.1 m/s | 2.582 Pa | 253 | 0.111 Pa
| 176221 | 150.0 CMH | 160 mmø | 2.1 m/s | 2.582 Pa | 617 | 0.269 Pa
207 | 158785 | 300.0 CMH | 250 mmø | 1.7 m/s | 1.733 Pa | 250 | 0.044 Pa | 0.044 Pa
208 | 156412 | 300.0 CMH | 200 mmø | 2.7 m/s | 4.231 Pa | 176 | 0.090 Pa | 0.468 Pa
| 156487 | 300.0 CMH | 200 mmø | 2.7 m/s | 4.231 Pa | 508 | 0.261 Pa
| 158422 | 300.0 CMH | 200 mmø | 2.7 m/s | 4.231 Pa | 151 | 0.078 Pa
| 2174656 | 300.0 CMH | 200 mmø | 2.7 m/s | 4.231 Pa | 74 | 0.038 Pa
209 | 173026 | 250.0 CMH | 200 mmø | 2.2 m/s | 2.938 Pa | 50 | 0.019 Pa | 0.369 Pa
| 173611 | 250.0 CMH | 200 mmø | 2.2 m/s | 2.938 Pa | 334 | 0.124 Pa
| 173818 | 250.0 CMH | 200 mmø | 2.2 m/s | 2.938 Pa | 99 | 0.037 Pa
| 174478 | 250.0 CMH | 200 mmø | 2.2 m/s | 2.938 Pa | 36 | 0.013 Pa
| 174574 | 250.0 CMH | 200 mmø | 2.2 m/s | 2.938 Pa | 247 | 0.092 Pa
| 174988 | 250.0 CMH | 200 mmø | 2.2 m/s | 2.938 Pa | 228 | 0.085 Pa
210 | 156535 | 100.0 CMH | 160 mmø | 1.4 m/s | 1.148 Pa | 637 | 0.135 Pa | 0.307 Pa
| 157516 | 100.0 CMH | 160 mmø | 1.4 m/s | 1.148 Pa | 305 | 0.065 Pa
| 158416 | 100.0 CMH | 160 mmø | 1.4 m/s | 1.148 Pa | 217 | 0.046 Pa
| 567518 | 100.0 CMH | 160 mm | 1.4 m/s | 1.148 Pa | 293 | 0.062 Pa
211 | 173035 | 100.0 CMH | 160 mmø | 1.4 m/s | 1.148 Pa | 280 | 0.059 Pa | 0.287 Pa
| 173113 | 100.0 CMH | 160 mmø | 1.4 m/s | 1.148 Pa | 449 | 0.095 Pa
| 173476 | 100.0 CMH | 160 mmø | 1.4 m/s | 1.148 Pa | 358 | 0.076 Pa
| 174964 | 100.0 CMH | 160 mmø | 1.4 m/s | 1.148 Pa | 114 | 0.024 Pa
| 175714 | 100.0 CMH | 160 mmø | 1.4 m/s | 1.148 Pa | 155 | 0.033 Pa
212 | 173164 | 100.0 CMH | 160 mmø | 1.4 m/s | 1.148 Pa | 305 | 0.065 Pa | 0.308 Pa
| 174778 | 100.0 CMH | 160 mmø | 1.4 m/s | 1.148 Pa | 637 | 0.135 Pa
| 176059 | 100.0 CMH | 160 mmø | 1.4 m/s | 1.148 Pa | 217 | 0.046 Pa
| 1607297 | 100.0 CMH | 160 mm | 1.4 m/s | 1.148 Pa | 296 | 0.063 Pa
213 | 174280 | 100.0 CMH | 160 mmø | 1.4 m/s | 1.148 Pa | 305 | 0.065 Pa | 0.310 Pa
| 174688 | 100.0 CMH | 160 mmø | 1.4 m/s | 1.148 Pa | 217 | 0.046 Pa
| 175531 | 100.0 CMH | 160 mmø | 1.4 m/s | 1.148 Pa | 637 | 0.135 Pa
| 1607325 | 100.0 CMH | 160 mm | 1.4 m/s | 1.148 Pa | 303 | 0.064 Pa
214 | 173278 | 100.0 CMH | 160 mmø | 1.4 m/s | 1.148 Pa | 277 | 0.059 Pa | 0.310 Pa
| 174040 | 100.0 CMH | 160 mmø | 1.4 m/s | 1.148 Pa | 292 | 0.062 Pa
| 174379 | 100.0 CMH | 160 mmø | 1.4 m/s | 1.148 Pa | 344 | 0.073 Pa
| 176041 | 100.0 CMH | 160 mmø | 1.4 m/s | 1.148 Pa | 244 | 0.052 Pa
| 1607320 | 100.0 CMH | 160 mm | 1.4 m/s | 1.148 Pa | 303 | 0.064 Pa
215 | 173449 | 300.0 CMH | 250 mmø | 1.7 m/s | 1.733 Pa | 212 | 0.037 Pa | 0.708 Pa
| 173674 | 300.0 CMH | 250 mmø | 1.7 m/s | 1.733 Pa | 302 | 0.053 Pa
| 173764 | 300.0 CMH | 250 mmø | 1.7 m/s | 1.733 Pa | 652 | 0.114 Pa
| 173839 | 300.0 CMH | 250 mmø | 1.7 m/s | 1.733 Pa | 1577 | 0.276 Pa
| 174700 | 300.0 CMH | 250 mmø | 1.7 m/s | 1.733 Pa | 128 | 0.022 Pa
| 175237 | 300.0 CMH | 250 mmø | 1.7 m/s | 1.733 Pa | 280 | 0.049 Pa
| 175276 | 300.0 CMH | 250 mmø | 1.7 m/s | 1.733 Pa | 92 | 0.016 Pa
| 175534 | 300.0 CMH | 250 mmø | 1.7 m/s | 1.733 Pa | 466 | 0.082 Pa
| 175633 | 300.0 CMH | 250 mmø | 1.7 m/s | 1.733 Pa | 245 | 0.043 Pa
| 2177385 | 300.0 CMH | 250 mmø | 1.7 m/s | 1.733 Pa | 89 | 0.016 Pa
216 | 160669 | 250.0 CMH | 250 mmø | 1.4 m/s | 1.203 Pa | 629 | 0.080 Pa | 0.377 Pa
| 161020 | 250.0 CMH | 250 mmø | 1.4 m/s | 1.203 Pa | 756 | 0.096 Pa
| 161818 | 250.0 CMH | 250 mmø | 1.4 m/s | 1.203 Pa | 348 | 0.044 Pa
| 162358 | 250.0 CMH | 250 mmø | 1.4 m/s | 1.203 Pa | 1083 | 0.137 Pa
| 2178001 | 250.0 CMH | 250 mmø | 1.4 m/s | 1.203 Pa | 159 | 0.020 Pa
Fitting and Accessory Loss Coefficient Summary by Sections
Section | Element ID | Loss Method | ASHRAE Table | Loss Coefficient | Pressure Loss | Total Pressure Loss
1 | 2505447 | Coefficient from ASHRAE Table | ER4-2 | 0 | 0.000 Pa | 0.000 Pa
2 | 2178978 | Coefficient from ASHRAE Table | SR5-11 | 0 | 0.000 Pa | 32.510 Pa
| 819777 | Coefficient from ASHRAE Table | ER3-1 | 1.15 | 9.796 Pa
| 819982 | Coefficient from ASHRAE Table | ER3-1 | 1.15 | 9.796 Pa
| 2212251 | Coefficient from ASHRAE Table | ER3-1 | 1.15 | 9.796 Pa
| 2505447 | Coefficient from ASHRAE Table | ER4-2 | 0.36655 | 3.122 Pa
3 | 460690 | Specific Loss | - | 0.66475 | 0.800 Pa | 3.622 Pa
| 698797 | Specific Loss | - | 0.66475 | 0.800 Pa
| 2636481 | Coefficient from ASHRAE Table | ED5-3 | 1.68 | 2.022 Pa
4 | 460693 | Specific Loss | - | 6.232 | 30.000 Pa | 184.236 Pa
| 460694 | Specific Loss | - | 31.1601 | 150.000 Pa
| 460695 | Specific Loss | - | 0.16619 | 0.800 Pa
| 656413 | Specific Loss | - | 0.16619 | 0.800 Pa
| 656416 | Coefficient from ASHRAE Table | - | 0 | 0.000 Pa
| 656428 | Coefficient from ASHRAE Table | - | 0 | 0.000 Pa
| 656466 | Coefficient from ASHRAE Table | ED5-3 | 0.54769 | 2.636 Pa
| 2636481 | Coefficient from ASHRAE Table | ED5-3 | 0 | 0.000 Pa
5 | 656466 | Coefficient from ASHRAE Table | ED5-3 | 0 | 0.000 Pa | 12.100 Pa
| 673987 | Specific Loss | - | 0.098335 | 0.800 Pa
| 673990 | Specific Loss | - | 0.098335 | 0.800 Pa
| 673992 | Specific Loss | - | 0.098335 | 0.800 Pa
| 2638811 | Coefficient from ASHRAE Table | ED5-3 | 1.1923 | 9.700 Pa
6 | 722536 | Coefficient from ASHRAE Table | ED5-3 | 0.0833 | 0.702 Pa | 0.702 Pa
| 2638811 | Coefficient from ASHRAE Table | ED5-3 | 0 | 0.000 Pa
7 | 722536 | Coefficient from ASHRAE Table | ED5-3 | 0 | 0.000 Pa | 153.200 Pa
| 722583 | Specific Loss | - | 0.07272 | 0.800 Pa
| 763554 | Coefficient from ASHRAE Table | - | 0 | 0.000 Pa
| 763557 | Specific Loss | - | 13.6351 | 150.000 Pa
| 763564 | Specific Loss | - | 0.07272 | 0.800 Pa
| 763569 | Specific Loss | - | 0.07272 | 0.800 Pa
| 763572 | Specific Loss | - | 0.07272 | 0.800 Pa
| 790302 | Coefficient from ASHRAE Table | - | 0 | 0.000 Pa
| 2175989 | Coefficient from ASHRAE Table | SR5-11 | 0 | 0.000 Pa
8 | 2175866 | Coefficient from ASHRAE Table | - | 0 | 0.000 Pa | 0.000 Pa
| 2175989 | Coefficient from ASHRAE Table | SR5-11 | 0 | 0.000 Pa
9 | 1589752 | Coefficient from ASHRAE Table | ER3-1 | 1.15 | 8.759 Pa | 17.518 Pa
| 1589767 | Coefficient from ASHRAE Table | ER3-1 | 1.15 | 8.759 Pa
| 2175866 | Coefficient from ASHRAE Table | - | 0 | 0.000 Pa
| 2175314 | Coefficient from ASHRAE Table | SR5-11 | 0 | 0.000 Pa
10 | 2175314 | Coefficient from ASHRAE Table | SR5-11 | 0 | 0.000 Pa | 0.000 Pa
| 1589779 | Coefficient from ASHRAE Table | - | 0 | 0.000 Pa
11 | 1589779 | Coefficient from ASHRAE Table | - | 0 | 0.000 Pa | 37.783 Pa
| 1606959 | Coefficient from ASHRAE Table | ER3-1 | 1.15 | 12.005 Pa
| 1606965 | Coefficient from ASHRAE Table | ER3-1 | 1.15 | 12.005 Pa
| 1667870 | Specific Loss | - | 0.95791 | 10.000 Pa
| 1667871 | Coefficient from ASHRAE Table | CR6-3 | 0 | 0.000 Pa
| 1829348 | Coefficient from ASHRAE Table | ER4-2 | 0.36135 | 3.772 Pa
12 | 1829348 | Coefficient from ASHRAE Table | ER4-2 | 0 | 0.000 Pa | 0.000 Pa
| 2176328 | Coefficient from ASHRAE Table | SR5-11 | 0 | 0.000 Pa
13 | 2176328 | Coefficient from ASHRAE Table | SR5-11 | 0 | 0.000 Pa | 1.066 Pa
| 1831391 | Coefficient from ASHRAE Table | ER4-2 | 0.12664 | 1.066 Pa
14 | 1831391 | Coefficient from ASHRAE Table | ER4-2 | 0 | 0.000 Pa | 0.000 Pa
| 2178557 | Coefficient from ASHRAE Table | SR5-11 | 0 | 0.000 Pa
15 | 2178557 | Coefficient from ASHRAE Table | SR5-11 | 0 | 0.000 Pa | 29.044 Pa
| 819884 | Coefficient from ASHRAE Table | ER4-2 | 0.0132 | 0.132 Pa
| 1913117 | Specific Loss | - | 0.99824 | 10.000 Pa
| 1913520 | Coefficient from ASHRAE Table | ER3-1 | 1.15 | 11.520 Pa
| 1913605 | Coefficient from ASHRAE Table | CR3-1 | 0.045377 | 0.455 Pa
| 1913652 | Coefficient from ASHRAE Table | CR3-17 | 0.69249 | 6.937 Pa
16 | 819761 | Coefficient from ASHRAE Table | ER3-1 | 1.21 | 11.641 Pa | 43.807 Pa
| 819884 | Coefficient from ASHRAE Table | ER4-2 | 0 | 0.000 Pa
| 820093 | Coefficient from ASHRAE Table | ER3-1 | 1.21 | 11.641 Pa
| 1009483 | Coefficient from ASHRAE Table | ER3-1 | 1.0667 | 10.262 Pa
| 1009484 | Coefficient from ASHRAE Table | ER3-1 | 1.0667 | 10.262 Pa
| 1912046 | Coefficient from ASHRAE Table | - | 0 | 0.000 Pa
17 | 1911675 | Coefficient from ASHRAE Table | - | 0 | 0.000 Pa | 0.000 Pa
| 1912046 | Coefficient from ASHRAE Table | - | 0 | 0.000 Pa
18 | 1903615 | Coefficient from ASHRAE Table | ER4-2 | 0.33 | 3.175 Pa | 23.700 Pa
| 1903631 | Coefficient from ASHRAE Table | ER3-1 | 1.0667 | 10.262 Pa
| 1903632 | Coefficient from ASHRAE Table | ER3-1 | 1.0667 | 10.262 Pa
| 1911675 | Coefficient from ASHRAE Table | - | 0 | 0.000 Pa
19 | 1903615 | Coefficient from ASHRAE Table | ER4-2 | 0 | 0.000 Pa | 0.000 Pa
| 2178978 | Coefficient from ASHRAE Table | SR5-11 | 0 | 0.000 Pa
20 | 982667 | Specific Loss | - | 0.69704 | 0.800 Pa | 183.046 Pa
| 982670 | Specific Loss | - | 0.69704 | 0.800 Pa
| 982672 | Specific Loss | - | 0.69704 | 0.800 Pa
| 982676 | Specific Loss | - | 130.6948 | 150.000 Pa
| 982677 | Specific Loss | - | 26.139 | 30.000 Pa
| 2638632 | Coefficient from ASHRAE Table | ED5-3 | 0.56328 | 0.646 Pa
21 | 893255 | Specific Loss | - | 0.33916 | 0.800 Pa | 5.142 Pa
| 893257 | Specific Loss | - | 0.33916 | 0.800 Pa
| 982689 | Coefficient from ASHRAE Table | - | 0 | 0.000 Pa
| 982705 | Specific Loss | - | 0.33916 | 0.800 Pa
| 982716 | Specific Loss | - | 0.33916 | 0.800 Pa
| 982719 | Coefficient from ASHRAE Table | ED5-3 | 0.82328 | 1.942 Pa
| 2638632 | Coefficient from ASHRAE Table | ED5-3 | 0 | 0.000 Pa
22 | 982719 | Coefficient from ASHRAE Table | ED5-3 | 0 | 0.000 Pa | 151.598 Pa
| 982763 | Specific Loss | - | 31.1601 | 150.000 Pa
| 982768 | Coefficient from ASHRAE Table | ED5-3 | 0.33187 | 1.598 Pa
23 | 982768 | Coefficient from ASHRAE Table | ED5-3 | 0 | 0.000 Pa | 13.072 Pa
| 982777 | Specific Loss | - | 0.11541 | 0.800 Pa
| 1589701 | Specific Loss | - | 0.11541 | 0.800 Pa
| 2235050 | Specific Loss | - | 0.11541 | 0.800 Pa
| 2235284 | Coefficient from ASHRAE Table | ED5-3 | 1.4241 | 9.872 Pa
| 2261687 | Specific Loss | - | 0.11541 | 0.800 Pa
24 | 2234212 | Coefficient from ASHRAE Table | ED4-2 | 0.21534 | 1.904 Pa | 1.904 Pa
| 2235284 | Coefficient from ASHRAE Table | ED5-3 | 0 | 0.000 Pa
25 | 2175989 | Coefficient from ASHRAE Table | SR5-11 | 0 | 0.000 Pa | 0.000 Pa
| 2234212 | Coefficient from ASHRAE Table | ED4-2 | 0 | 0.000 Pa
26 | 982719 | Coefficient from ASHRAE Table | ED5-3 | 0.76656 | 1.980 Pa | 184.380 Pa
| 982735 | Specific Loss | - | 58.0866 | 150.000 Pa
| 982736 | Specific Loss | - | 11.6173 | 30.000 Pa
| 982743 | Specific Loss | - | 0.30979 | 0.800 Pa
| 982746 | Specific Loss | - | 0.30979 | 0.800 Pa
| 982757 | Specific Loss | - | 0.30979 | 0.800 Pa
| 982760 | Coefficient from ASHRAE Table | - | 0 | 0.000 Pa
27 | 982768 | Coefficient from ASHRAE Table | ED5-3 | -4.0791 | -4.682 Pa | 177.718 Pa
| 982780 | Specific Loss | - | 0.69704 | 0.800 Pa
| 982783 | Specific Loss | - | 0.69704 | 0.800 Pa
| 982785 | Specific Loss | - | 0.69704 | 0.800 Pa
| 982789 | Coefficient from ASHRAE Table | - | 0 | 0.000 Pa
| 982792 | Specific Loss | - | 130.6948 | 150.000 Pa
| 982793 | Specific Loss | - | 26.139 | 30.000 Pa
28 | 460660 | Specific Loss | - | 0.66475 | 0.800 Pa | 7.111 Pa
| 460663 | Specific Loss | - | 0.66475 | 0.800 Pa
| 460666 | Coefficient from ASHRAE Table | - | 0 | 0.000 Pa
| 460670 | Specific Loss | - | 0.66475 | 0.800 Pa
| 460674 | Specific Loss | - | 0.66475 | 0.800 Pa
| 460679 | Specific Loss | - | 0.66475 | 0.800 Pa
| 674043 | Specific Loss | - | 0.66475 | 0.800 Pa
| 674046 | Coefficient from ASHRAE Table | - | 0 | 0.000 Pa
| 2636481 | Coefficient from ASHRAE Table | ED5-3 | 1.92 | 2.311 Pa
29 | 845407 | Specific Loss | - | 0.4461 | 0.800 Pa | 0.800 Pa
| 845410 | Coefficient from ASHRAE Table | - | 0 | 0.000 Pa
| 845413 | Coefficient from ASHRAE Table | - | 0 | 0.000 Pa
| 893202 | Coefficient from ASHRAE Table | SD5-24 | 0 | 0.000 Pa
30 | 893197 | Specific Loss | - | 0.11153 | 0.800 Pa | 205.333 Pa
| 893202 | Coefficient from ASHRAE Table | SD5-24 | 2.9276 | 21.000 Pa
| 893241 | Specific Loss | - | 0.11153 | 0.800 Pa
| 893248 | Specific Loss | - | 20.9112 | 150.000 Pa
| 893251 | Specific Loss | - | 4.1822 | 30.000 Pa
| 982683 | Coefficient from ASHRAE Table | ED4-1 | 0.38104 | 2.733 Pa
31 | 982683 | Coefficient from ASHRAE Table | ED4-1 | 0 | 0.000 Pa | 0.922 Pa
| 982686 | Coefficient from ASHRAE Table | - | 0 | 0.000 Pa
| 2638632 | Coefficient from ASHRAE Table | ED5-3 | 0.76641 | 0.922 Pa
32 | 656456 | Specific Loss | - | 11.6173 | 30.000 Pa | 181.836 Pa
| 656457 | Specific Loss | - | 58.0866 | 150.000 Pa
| 656458 | Specific Loss | - | 0.30979 | 0.800 Pa
| 656461 | Specific Loss | - | 0.30979 | 0.800 Pa
| 656466 | Coefficient from ASHRAE Table | ED5-3 | -0.21857 | -0.564 Pa
| 656485 | Specific Loss | - | 0.30979 | 0.800 Pa
33 | 893202 | Coefficient from ASHRAE Table | SD5-24 | 0 | 0.000 Pa | 0.000 Pa
| 893205 | Coefficient from ASHRAE Table | - | 0 | 0.000 Pa
| 893208 | Coefficient from ASHRAE Table | - | 0 | 0.000 Pa
34 | 355085 | Specific Loss | - | 0.25967 | 0.800 Pa | 186.331 Pa
| 355087 | Specific Loss | - | 0.25967 | 0.800 Pa
| 355091 | Specific Loss | - | 0.25967 | 0.800 Pa
| 460637 | Specific Loss | - | 0.25967 | 0.800 Pa
| 460642 | Specific Loss | - | 0.25967 | 0.800 Pa
| 460644 | Specific Loss | - | 0.25967 | 0.800 Pa
| 460648 | Specific Loss | - | 9.7375 | 30.000 Pa
| 460649 | Specific Loss | - | 48.6876 | 150.000 Pa
| 674001 | Coefficient from ASHRAE Table | ED4-1 | 0.23715 | 0.731 Pa
| 674017 | Coefficient from ASHRAE Table | - | 0 | 0.000 Pa
| 674020 | Coefficient from ASHRAE Table | - | 0 | 0.000 Pa
| 674023 | Specific Loss | - | 0.25967 | 0.800 Pa
| 674029 | Coefficient from ASHRAE Table | - | 0 | 0.000 Pa
| 698810 | Coefficient from ASHRAE Table | - | 0 | 0.000 Pa
35 | 674001 | Coefficient from ASHRAE Table | ED4-1 | 0 | 0.000 Pa | 5.866 Pa
| 674004 | Coefficient from ASHRAE Table | - | 0 | 0.000 Pa
| 2638811 | Coefficient from ASHRAE Table | ED5-3 | 4.799 | 5.866 Pa
36 | 707144 | Specific Loss | - | 0.30979 | 0.800 Pa | 178.652 Pa
| 707148 | Specific Loss | - | 11.6173 | 30.000 Pa
| 707149 | Specific Loss | - | 58.0866 | 150.000 Pa
| 707175 | Specific Loss | - | 0.30979 | 0.800 Pa
| 707178 | Coefficient from ASHRAE Table | - | 0 | 0.000 Pa
| 707182 | Coefficient from ASHRAE Table | - | 0 | 0.000 Pa
| 722525 | Specific Loss | - | 0.30979 | 0.800 Pa
| 722528 | Specific Loss | - | 0.30979 | 0.800 Pa
| 722530 | Specific Loss | - | 0.30979 | 0.800 Pa
| 722536 | Coefficient from ASHRAE Table | ED5-3 | -2.071 | -5.348 Pa
37 | 1514063 | Coefficient from ASHRAE Table | - | 0 | 0.000 Pa | 8.487 Pa
| 1514068 | Specific Loss | - | 0.17426 | 0.800 Pa
| 1514071 | Specific Loss | - | 0.17426 | 0.800 Pa
| 2640288 | Coefficient from ASHRAE Table | ED5-3 | 1.5001 | 6.887 Pa
38 | 1513983 | Specific Loss | - | 0.069783 | 0.800 Pa | 188.335 Pa
| 1513986 | Specific Loss | - | 0.069783 | 0.800 Pa
| 1513992 | Specific Loss | - | 0.069783 | 0.800 Pa
| 1513998 | Specific Loss | - | 0.069783 | 0.800 Pa
| 1514007 | Specific Loss | - | 0.069783 | 0.800 Pa
| 1514061 | Specific Loss | - | 13.0842 | 150.000 Pa
| 1514062 | Specific Loss | - | 2.6168 | 30.000 Pa
| 1722194 | Specific Loss | - | 0.069783 | 0.800 Pa
| 1722198 | Coefficient from ASHRAE Table | - | 0 | 0.000 Pa
| 1772507 | Coefficient from ASHRAE Table | ED4-1 | 0.30834 | 3.535 Pa
| 2640288 | Coefficient from ASHRAE Table | ED5-3 | 0 | 0.000 Pa
39 | 1772501 | Coefficient from ASHRAE Table | - | 0 | 0.000 Pa | 5.915 Pa
| 1772507 | Coefficient from ASHRAE Table | ED4-1 | 0 | 0.000 Pa
| 2640058 | Coefficient from ASHRAE Table | ED5-3 | 1.92 | 5.915 Pa
40 | 1772539 | Specific Loss | - | 0.064917 | 0.800 Pa | 3.520 Pa
| 1772542 | Specific Loss | - | 0.064917 | 0.800 Pa
| 1772547 | Specific Loss | - | 0.064917 | 0.800 Pa
| 1772560 | Coefficient from ASHRAE Table | - | 0 | 0.000 Pa
| 1772581 | Coefficient from ASHRAE Table | ED4-1 | 0.090881 | 1.120 Pa
| 2640058 | Coefficient from ASHRAE Table | ED5-3 | 0 | 0.000 Pa
41 | 1772581 | Coefficient from ASHRAE Table | ED4-1 | 0 | 0.000 Pa | 1.302 Pa
| 2236143 | Coefficient from ASHRAE Table | ED5-3 | 0.16623 | 1.302 Pa
42 | 1803490 | Specific Loss | - | 0.072437 | 0.800 Pa | 4.800 Pa
| 1803492 | Specific Loss | - | 0.072437 | 0.800 Pa
| 1803553 | Specific Loss | - | 0.072437 | 0.800 Pa
| 1803555 | Specific Loss | - | 0.072437 | 0.800 Pa
| 1803664 | Specific Loss | - | 0.072437 | 0.800 Pa
| 1803666 | Specific Loss | - | 0.072437 | 0.800 Pa
| 2178642 | Coefficient from ASHRAE Table | SR5-11 | 0 | 0.000 Pa
| 2236143 | Coefficient from ASHRAE Table | ED5-3 | 0 | 0.000 Pa
43 | 2178642 | Coefficient from ASHRAE Table | SR5-11 | 0 | 0.000 Pa | 18.383 Pa
| 1805242 | Coefficient from ASHRAE Table | ER3-1 | 1.15 | 9.192 Pa
| 1805253 | Coefficient from ASHRAE Table | ER3-1 | 1.15 | 9.192 Pa
| 1805273 | Coefficient from ASHRAE Table | - | 0 | 0.000 Pa
44 | 1805273 | Coefficient from ASHRAE Table | - | 0 | 0.000 Pa | 0.000 Pa
| 2178604 | Coefficient from ASHRAE Table | SR5-11 | 0 | 0.000 Pa
45 | 2178604 | Coefficient from ASHRAE Table | SR5-11 | 0 | 0.000 Pa | 11.736 Pa
| 1805288 | Coefficient from ASHRAE Table | CR3-1 | 0.086706 | 0.868 Pa
| 1805291 | Coefficient from ASHRAE Table | CR3-1 | 0.086706 | 0.868 Pa
| 1806351 | Specific Loss | - | 0.99911 | 10.000 Pa
| 1806486 | Coefficient from ASHRAE Table | - | 0 | 0.000 Pa
46 | 1806486 | Coefficient from ASHRAE Table | - | 0 | 0.000 Pa | 7.186 Pa
| 2178554 | Coefficient from ASHRAE Table | ER3-1 | 1.15 | 7.186 Pa
| 2178557 | Coefficient from ASHRAE Table | SR5-11 | 0 | 0.000 Pa
47 | 1237404 | Specific Loss | - | 0.66475 | 0.800 Pa | 181.600 Pa
| 1684953 | Specific Loss | - | 124.6402 | 150.000 Pa
| 1684954 | Specific Loss | - | 24.928 | 30.000 Pa
| 1684955 | Specific Loss | - | 0.66475 | 0.800 Pa
| 1684959 | Coefficient from ASHRAE Table | CD3-11 | 0 | 0.000 Pa
| 2177312 | Coefficient from ASHRAE Table | SR5-11 | 0 | 0.000 Pa
48 | 2177312 | Coefficient from ASHRAE Table | SR5-11 | 0 | 0.000 Pa | 10.000 Pa
| 1588080 | Coefficient from ASHRAE Table | CR6-3 | 0 | 0.000 Pa
| 1588086 | Specific Loss | - | 0.88295 | 10.000 Pa
| 1588122 | Coefficient from ASHRAE Table | - | 0 | 0.000 Pa
49 | 1588122 | Coefficient from ASHRAE Table | - | 0 | 0.000 Pa | 0.000 Pa
| 2177056 | Coefficient from ASHRAE Table | SR5-11 | 0 | 0.000 Pa
50 | 2177056 | Coefficient from ASHRAE Table | SR5-11 | 0 | 0.000 Pa | 1.810 Pa
| 1885531 | Coefficient from ASHRAE Table | ER4-2 | 0.1451 | 1.810 Pa
51 | 2177923 | Coefficient from ASHRAE Table | - | 0 | 0.000 Pa | 0.000 Pa
| 1885531 | Coefficient from ASHRAE Table | ER4-2 | 0 | 0.000 Pa
52 | 2177923 | Coefficient from ASHRAE Table | - | 0 | 0.000 Pa | 60.852 Pa
| 819757 | Coefficient from ASHRAE Table | ER3-1 | 1.15 | 16.599 Pa
| 819779 | Coefficient from ASHRAE Table | CR3-1 | 0.10374 | 1.497 Pa
| 1190850 | Specific Loss | - | 0.69282 | 10.000 Pa
| 1190884 | Coefficient from ASHRAE Table | ER3-1 | 1.15 | 16.599 Pa
| 1903656 | Coefficient from ASHRAE Table | CR3-17 | 1.1194 | 16.157 Pa
| 2178978 | Coefficient from ASHRAE Table | SR5-11 | 0 | 0.000 Pa
53 | 1784718 | Coefficient from ASHRAE Table | ED5-4 | 2.52 | 3.033 Pa | 4.633 Pa
| 1784733 | Specific Loss | - | 0.66475 | 0.800 Pa
| 1784736 | Specific Loss | - | 0.66475 | 0.800 Pa
54 | 1784718 | Coefficient from ASHRAE Table | ED5-4 | 0 | 0.000 Pa | 185.598 Pa
| 1784721 | Specific Loss | - | 0.16619 | 0.800 Pa
| 1784723 | Specific Loss | - | 0.16619 | 0.800 Pa
| 1784727 | Specific Loss | - | 0.16619 | 0.800 Pa
| 1784730 | Specific Loss | - | 0.16619 | 0.800 Pa
| 1784755 | Specific Loss | - | 0.16619 | 0.800 Pa
| 1784760 | Specific Loss | - | 31.1601 | 150.000 Pa
| 1784761 | Specific Loss | - | 6.232 | 30.000 Pa
| 1784763 | Coefficient from ASHRAE Table | ED5-3 | 0.33187 | 1.598 Pa
55 | 1784763 | Coefficient from ASHRAE Table | ED5-3 | 0 | 0.000 Pa | 2.947 Pa
| 1784895 | Coefficient from ASHRAE Table | ED5-3 | 0.4252 | 2.947 Pa
56 | 1784895 | Coefficient from ASHRAE Table | ED5-3 | 0 | 0.000 Pa | 2.108 Pa
| 1784949 | Coefficient from ASHRAE Table | ED5-3 | 0.19461 | 2.108 Pa
57 | 1784949 | Coefficient from ASHRAE Table | ED5-3 | 0 | 0.000 Pa | 0.000 Pa
| 1805184 | Coefficient from ASHRAE Table | - | 0 | 0.000 Pa
58 | 2178792 | Coefficient from ASHRAE Table | SR5-11 | 0 | 0.000 Pa | 0.000 Pa
| 1805184 | Coefficient from ASHRAE Table | - | 0 | 0.000 Pa
59 | 2178792 | Coefficient from ASHRAE Table | SR5-11 | 0 | 0.000 Pa | 0.000 Pa
| 2178743 | Coefficient from ASHRAE Table | SR5-11 | 0 | 0.000 Pa
60 | 2178743 | Coefficient from ASHRAE Table | SR5-11 | 0 | 0.000 Pa | 0.475 Pa
| 1805191 | Coefficient from ASHRAE Table | ER4-2 | 0.062748 | 0.475 Pa
61 | 1805186 | Coefficient from ASHRAE Table | ER3-1 | 1.2014 | 15.045 Pa | 15.045 Pa
| 1805191 | Coefficient from ASHRAE Table | ER4-2 | 0 | 0.000 Pa
| 1805198 | Coefficient from ASHRAE Table | - | 0 | 0.000 Pa
62 | 1805198 | Coefficient from ASHRAE Table | - | 0 | 0.000 Pa | 6.880 Pa
| 1805211 | Coefficient from ASHRAE Table | CR3-1 | 0.081473 | 1.020 Pa
| 1805219 | Coefficient from ASHRAE Table | CR3-1 | 0.0964 | 1.207 Pa
| 1805233 | Coefficient from ASHRAE Table | ER4-2 | 0.37157 | 4.653 Pa
63 | 2178642 | Coefficient from ASHRAE Table | SR5-11 | 0 | 0.000 Pa | 0.000 Pa
| 1805233 | Coefficient from ASHRAE Table | ER4-2 | 0 | 0.000 Pa
64 | 1712798 | Specific Loss | - | 0.30979 | 0.800 Pa | 177.620 Pa
| 1712801 | Specific Loss | - | 11.6173 | 30.000 Pa
| 1712807 | Specific Loss | - | 58.0866 | 150.000 Pa
| 2214272 | Coefficient from ASHRAE Table | ED5-3 | -1.5413 | -3.980 Pa
| 2214281 | Specific Loss | - | 0.30979 | 0.800 Pa
65 | 2214198 | Coefficient from ASHRAE Table | - | 0 | 0.000 Pa | 0.000 Pa
| 2214272 | Coefficient from ASHRAE Table | ED5-3 | 0 | 0.000 Pa
66 | 1712751 | Specific Loss | - | 0.080709 | 0.800 Pa | 7.515 Pa
| 1712754 | Specific Loss | - | 0.080709 | 0.800 Pa
| 1712756 | Coefficient from ASHRAE Table | ED4-2 | 0.35462 | 3.515 Pa
| 1712763 | Specific Loss | - | 0.080709 | 0.800 Pa
| 1712768 | Specific Loss | - | 0.080709 | 0.800 Pa
| 1712771 | Coefficient from ASHRAE Table | - | 0 | 0.000 Pa
| 2214195 | Specific Loss | - | 0.080709 | 0.800 Pa
| 2214198 | Coefficient from ASHRAE Table | - | 0 | 0.000 Pa
67 | 1712756 | Coefficient from ASHRAE Table | ED4-2 | 0 | 0.000 Pa | 0.000 Pa
| 2176432 | Coefficient from ASHRAE Table | SR5-11 | 0 | 0.000 Pa
68 | 2176432 | Coefficient from ASHRAE Table | SR5-11 | 0 | 0.000 Pa | 0.000 Pa
| 2176394 | Coefficient from ASHRAE Table | SR5-11 | 0 | 0.000 Pa
69 | 2176394 | Coefficient from ASHRAE Table | SR5-11 | 0 | 0.000 Pa | 35.021 Pa
| 1744389 | Coefficient from ASHRAE Table | ER3-1 | 1.15 | 12.511 Pa
| 1744406 | Coefficient from ASHRAE Table | ER3-1 | 1.15 | 12.511 Pa
| 1746720 | Coefficient from ASHRAE Table | CR6-3 | 0 | 0.000 Pa
| 1746722 | Specific Loss | - | 0.91921 | 10.000 Pa
| 1746723 | Coefficient from ASHRAE Table | - | 0 | 0.000 Pa
70 | 1746723 | Coefficient from ASHRAE Table | - | 0 | 0.000 Pa | 7.810 Pa
| 2176325 | Coefficient from ASHRAE Table | ER3-1 | 1.15 | 7.810 Pa
| 2176328 | Coefficient from ASHRAE Table | SR5-11 | 0 | 0.000 Pa
71 | 1712822 | Specific Loss | - | 11.6173 | 30.000 Pa | 181.438 Pa
| 1722567 | Specific Loss | - | 58.0866 | 150.000 Pa
| 1722576 | Specific Loss | - | 0.30979 | 0.800 Pa
| 2261619 | Coefficient from ASHRAE Table | ED5-3 | -0.062857 | -0.162 Pa
| 2261626 | Specific Loss | - | 0.30979 | 0.800 Pa
72 | 2214272 | Coefficient from ASHRAE Table | ED5-3 | 0.18687 | 1.286 Pa | 1.286 Pa
| 2261619 | Coefficient from ASHRAE Table | ED5-3 | 0 | 0.000 Pa
73 | 1712842 | Coefficient from ASHRAE Table | ED5-3 | -4.0791 | -4.682 Pa | 176.918 Pa
| 1712910 | Specific Loss | - | 26.139 | 30.000 Pa
| 1712959 | Specific Loss | - | 130.6948 | 150.000 Pa
| 1713865 | Specific Loss | - | 0.69704 | 0.800 Pa
| 1713868 | Specific Loss | - | 0.69704 | 0.800 Pa
74 | 1712842 | Coefficient from ASHRAE Table | ED5-3 | 0 | 0.000 Pa | 0.325 Pa
| 2261569 | Coefficient from ASHRAE Table | ED4-1 | 0.046923 | 0.325 Pa
75 | 2261569 | Coefficient from ASHRAE Table | ED4-1 | 0 | 0.000 Pa | 1.169 Pa
| 2261619 | Coefficient from ASHRAE Table | ED5-3 | 0.26531 | 1.169 Pa
76 | 1713395 | Specific Loss | - | 11.6173 | 30.000 Pa | 183.580 Pa
| 1713396 | Specific Loss | - | 58.0866 | 150.000 Pa
| 1713397 | Coefficient from ASHRAE Table | ED5-3 | 0.76656 | 1.980 Pa
| 1713859 | Specific Loss | - | 0.30979 | 0.800 Pa
| 1713862 | Specific Loss | - | 0.30979 | 0.800 Pa
77 | 1712842 | Coefficient from ASHRAE Table | ED5-3 | 0.33187 | 1.598 Pa | 1.598 Pa
| 1713397 | Coefficient from ASHRAE Table | ED5-3 | 0 | 0.000 Pa
78 | 1713456 | Specific Loss | - | 26.139 | 30.000 Pa | 182.246 Pa
| 1713501 | Specific Loss | - | 130.6948 | 150.000 Pa
| 1713856 | Specific Loss | - | 0.69704 | 0.800 Pa
| 2214633 | Coefficient from ASHRAE Table | ED5-3 | 0.56328 | 0.646 Pa
| 2214644 | Specific Loss | - | 0.69704 | 0.800 Pa
79 | 1713397 | Coefficient from ASHRAE Table | ED5-3 | 0.82328 | 1.942 Pa | 1.942 Pa
| 2214633 | Coefficient from ASHRAE Table | ED5-3 | 0 | 0.000 Pa
80 | 1562545 | Specific Loss | - | 0.58454 | 0.800 Pa | 3.428 Pa
| 1562547 | Coefficient from ASHRAE Table | - | 0 | 0.000 Pa
| 1562550 | Coefficient from ASHRAE Table | - | 0 | 0.000 Pa
| 2215170 | Coefficient from ASHRAE Table | ED5-3 | 1.92 | 2.628 Pa
81 | 2215170 | Coefficient from ASHRAE Table | ED5-3 | 0 | 0.000 Pa | 3.467 Pa
| 2215371 | Coefficient from ASHRAE Table | ED5-3 | 0.63333 | 3.467 Pa
82 | 1562611 | Specific Loss | - | 0.064949 | 0.800 Pa | 2.186 Pa
| 1562614 | Coefficient from ASHRAE Table | ED4-1 | 0.1125 | 1.386 Pa
| 2215371 | Coefficient from ASHRAE Table | ED5-3 | 0 | 0.000 Pa
83 | 1562614 | Coefficient from ASHRAE Table | ED4-1 | 0 | 0.000 Pa | 186.229 Pa
| 1562617 | Coefficient from ASHRAE Table | ED4-1 | 0.20714 | 6.229 Pa
| 1562622 | Coefficient from ASHRAE Table | - | 0 | 0.000 Pa
| 1562625 | Specific Loss | - | 0.99762 | 30.000 Pa
| 1562626 | Specific Loss | - | 4.9881 | 150.000 Pa
84 | 1562617 | Coefficient from ASHRAE Table | ED4-1 | 0 | 0.000 Pa | 4.000 Pa
| 1562638 | Specific Loss | - | 0.064949 | 0.800 Pa
| 1562641 | Specific Loss | - | 0.064949 | 0.800 Pa
| 1562643 | Specific Loss | - | 0.064949 | 0.800 Pa
| 1562647 | Coefficient from ASHRAE Table | - | 0 | 0.000 Pa
| 1562649 | Specific Loss | - | 0.064949 | 0.800 Pa
| 1562651 | Specific Loss | - | 0.064949 | 0.800 Pa
85 | 1562647 | Coefficient from ASHRAE Table | - | 0 | 0.000 Pa | 0.000 Pa
| 2177500 | Coefficient from ASHRAE Table | SR5-11 | 0 | 0.000 Pa
86 | 2177500 | Coefficient from ASHRAE Table | SR5-11 | 0 | 0.000 Pa | 0.000 Pa
| 1577093 | Coefficient from ASHRAE Table | - | 0 | 0.000 Pa
87 | 1562732 | Coefficient from ASHRAE Table | ER3-1 | 1.15 | 13.846 Pa | 41.405 Pa
| 1562790 | Coefficient from ASHRAE Table | CR3-1 | 0.11469 | 1.381 Pa
| 1562791 | Coefficient from ASHRAE Table | CR3-17 | 0.81615 | 9.826 Pa
| 1564726 | Coefficient from ASHRAE Table | ER4-2 | 0.20815 | 2.506 Pa
| 1564734 | Coefficient from ASHRAE Table | ER3-1 | 1.15 | 13.846 Pa
| 1577093 | Coefficient from ASHRAE Table | - | 0 | 0.000 Pa
88 | 1564726 | Coefficient from ASHRAE Table | ER4-2 | 0 | 0.000 Pa | 0.000 Pa
| 2177388 | Coefficient from ASHRAE Table | SR5-11 | 0 | 0.000 Pa
89 | 2177388 | Coefficient from ASHRAE Table | SR5-11 | 0 | 0.000 Pa | 0.000 Pa
| 2177371 | Coefficient from ASHRAE Table | SR5-11 | 0 | 0.000 Pa
90 | 2177371 | Coefficient from ASHRAE Table | SR5-11 | 0 | 0.000 Pa | 0.000 Pa
| 1577099 | Coefficient from ASHRAE Table | - | 0 | 0.000 Pa
91 | 1577099 | Coefficient from ASHRAE Table | - | 0 | 0.000 Pa | 0.000 Pa
| 2177312 | Coefficient from ASHRAE Table | SR5-11 | 0 | 0.000 Pa
92 | 1607283 | Specific Loss | - | 130.6948 | 150.000 Pa | 180.800 Pa
| 1607284 | Specific Loss | - | 26.139 | 30.000 Pa
| 1607285 | Specific Loss | - | 0.69704 | 0.800 Pa
| 2177732 | Coefficient from ASHRAE Table | SR5-11 | 0 | 0.000 Pa
93 | 2177732 | Coefficient from ASHRAE Table | SR5-11 | 0 | 0.000 Pa | 0.000 Pa
| 2177695 | Coefficient from ASHRAE Table | SR5-11 | 0 | 0.000 Pa
94 | 2177695 | Coefficient from ASHRAE Table | SR5-11 | 0 | 0.000 Pa | 0.000 Pa
| 2177658 | Coefficient from ASHRAE Table | SR5-11 | 0 | 0.000 Pa
95 | 2177658 | Coefficient from ASHRAE Table | SR5-11 | 0 | 0.000 Pa | 0.000 Pa
| 2177599 | Coefficient from ASHRAE Table | SR5-11 | 0 | 0.000 Pa
96 | 2177599 | Coefficient from ASHRAE Table | SR5-11 | 0 | 0.000 Pa | 0.000 Pa
| 1621081 | Coefficient from ASHRAE Table | - | 0 | 0.000 Pa
97 | 1621061 | Coefficient from ASHRAE Table | CR3-17 | 1.4165 | 17.354 Pa | 32.286 Pa
| 1621063 | Coefficient from ASHRAE Table | ER3-1 | 1.15 | 14.090 Pa
| 1621065 | Coefficient from ASHRAE Table | CR3-1 | 0.068706 | 0.842 Pa
| 1621081 | Coefficient from ASHRAE Table | - | 0 | 0.000 Pa
| 1621122 | Coefficient from ASHRAE Table | - | 0 | 0.000 Pa
98 | 1621118 | Coefficient from ASHRAE Table | - | 0 | 0.000 Pa | 30.000 Pa
| 1621122 | Coefficient from ASHRAE Table | - | 0 | 0.000 Pa
| 1621130 | Specific Loss | - | 5.9781 | 30.000 Pa
99 | 1621100 | Coefficient from ASHRAE Table | ER3-1 | 1.15 | 14.090 Pa | 178.179 Pa
| 1621108 | Coefficient from ASHRAE Table | ER3-1 | 1.15 | 14.090 Pa
| 1621110 | Coefficient from ASHRAE Table | - | 0 | 0.000 Pa
| 1621115 | Specific Loss | - | 12.2431 | 150.000 Pa
| 1621118 | Coefficient from ASHRAE Table | - | 0 | 0.000 Pa
100 | 1621110 | Coefficient from ASHRAE Table | - | 0 | 0.000 Pa | 0.000 Pa
| 2177500 | Coefficient from ASHRAE Table | SR5-11 | 0 | 0.000 Pa
101 | 1722088 | Specific Loss | - | 0.58454 | 0.800 Pa | 3.899 Pa
| 1722091 | Specific Loss | - | 0.58454 | 0.800 Pa
| 1722105 | Coefficient from ASHRAE Table | ED5-3 | 1.68 | 2.299 Pa
102 | 1722105 | Coefficient from ASHRAE Table | ED5-3 | 0 | 0.000 Pa | 5.067 Pa
| 1722112 | Specific Loss | - | 0.14614 | 0.800 Pa
| 1722115 | Specific Loss | - | 0.14614 | 0.800 Pa
| 2637970 | Coefficient from ASHRAE Table | ED5-3 | 0.63333 | 3.467 Pa
103 | 1784686 | Specific Loss | - | 0.064949 | 0.800 Pa | 2.186 Pa
| 1784688 | Coefficient from ASHRAE Table | ED4-1 | 0.1125 | 1.386 Pa
| 2637970 | Coefficient from ASHRAE Table | ED5-3 | 0 | 0.000 Pa
104 | 1784683 | Specific Loss | - | 4.9881 | 150.000 Pa | 190.695 Pa
| 1784685 | Specific Loss | - | 0.99762 | 30.000 Pa
| 1784688 | Coefficient from ASHRAE Table | ED4-1 | 0 | 0.000 Pa
| 1784700 | Coefficient from ASHRAE Table | ED4-2 | 0.35565 | 10.695 Pa
105 | 1784695 | Coefficient from ASHRAE Table | - | 0 | 0.000 Pa | 0.000 Pa
| 1784700 | Coefficient from ASHRAE Table | ED4-2 | 0 | 0.000 Pa
106 | 1784656 | Coefficient from ASHRAE Table | ER3-1 | 1.15 | 4.214 Pa | 4.214 Pa
| 1784695 | Coefficient from ASHRAE Table | - | 0 | 0.000 Pa
| 2178231 | Coefficient from ASHRAE Table | SR5-11 | 0 | 0.000 Pa
107 | 2178231 | Coefficient from ASHRAE Table | SR5-11 | 0 | 0.000 Pa | 41.323 Pa
| 1793078 | Coefficient from ASHRAE Table | ER3-1 | 1.15 | 13.846 Pa
| 1793198 | Coefficient from ASHRAE Table | CR3-1 | 0.11469 | 1.381 Pa
| 1793205 | Coefficient from ASHRAE Table | CR3-17 | 0.81615 | 9.826 Pa
| 1793758 | Coefficient from ASHRAE Table | ER4-2 | 0.20136 | 2.424 Pa
| 1793871 | Coefficient from ASHRAE Table | ER3-1 | 1.15 | 13.846 Pa
108 | 1793758 | Coefficient from ASHRAE Table | ER4-2 | 0 | 0.000 Pa | 0.000 Pa
109 | 2178004 | Coefficient from ASHRAE Table | SR5-11 | 0 | 0.000 Pa | 0.000 Pa
110 | 2178004 | Coefficient from ASHRAE Table | SR5-11 | 0 | 0.000 Pa | 10.691 Pa
| 1829522 | Coefficient from ASHRAE Table | CR6-3 | 0 | 0.000 Pa
| 1829528 | Specific Loss | - | 1.0901 | 10.000 Pa
| 1832258 | Coefficient from ASHRAE Table | CR3-1 | 0.03767 | 0.346 Pa
| 1832264 | Coefficient from ASHRAE Table | CR3-1 | 0.03767 | 0.346 Pa
| 1832267 | Coefficient from ASHRAE Table | - | 0 | 0.000 Pa
111 | 1832267 | Coefficient from ASHRAE Table | - | 0 | 0.000 Pa | 0.000 Pa
| 2177923 | Coefficient from ASHRAE Table | - | 0 | 0.000 Pa
112 | 1514089 | Coefficient from ASHRAE Table | ED4-1 | 0.079256 | 0.364 Pa | 2.764 Pa
| 1514094 | Specific Loss | - | 0.17426 | 0.800 Pa
| 1514097 | Specific Loss | - | 0.17426 | 0.800 Pa
| 1514104 | Specific Loss | - | 0.17426 | 0.800 Pa
| 1514113 | Coefficient from ASHRAE Table | - | 0 | 0.000 Pa
113 | 1514084 | Coefficient from ASHRAE Table | - | 0 | 0.000 Pa | 5.835 Pa
| 1514089 | Coefficient from ASHRAE Table | ED4-1 | 0 | 0.000 Pa
| 2640288 | Coefficient from ASHRAE Table | ED5-3 | 2.0359 | 5.835 Pa
114 | 1784895 | Coefficient from ASHRAE Table | ED5-3 | -0.6564 | -1.695 Pa | 179.905 Pa
| 1784897 | Specific Loss | - | 0.30979 | 0.800 Pa
| 1784899 | Specific Loss | - | 58.0866 | 150.000 Pa
| 1784900 | Specific Loss | - | 11.6173 | 30.000 Pa
| 1784901 | Specific Loss | - | 0.30979 | 0.800 Pa
115 | 1784718 | Coefficient from ASHRAE Table | ED5-4 | 2.52 | 3.033 Pa | 4.633 Pa
| 1784739 | Specific Loss | - | 0.66475 | 0.800 Pa
| 1784741 | Specific Loss | - | 0.66475 | 0.800 Pa
116 | 1722121 | Specific Loss | - | 0.58454 | 0.800 Pa | 0.663 Pa
| 2637970 | Coefficient from ASHRAE Table | ED5-3 | -0.1 | -0.137 Pa
117 | 1722049 | Specific Loss | - | 0.58454 | 0.800 Pa | 5.028 Pa
| 1722052 | Specific Loss | - | 0.58454 | 0.800 Pa
| 1722055 | Coefficient from ASHRAE Table | - | 0 | 0.000 Pa
| 1722066 | Specific Loss | - | 0.58454 | 0.800 Pa
| 1722105 | Coefficient from ASHRAE Table | ED5-3 | 1.92 | 2.628 Pa
118 | 390897 | Specific Loss | - | 0.30979 | 0.800 Pa | 7.358 Pa
| 390900 | Specific Loss | - | 0.30979 | 0.800 Pa
| 407940 | Specific Loss | - | 0.30979 | 0.800 Pa
| 2216971 | Coefficient from ASHRAE Table | ED5-3 | 1.92 | 4.958 Pa
119 | 390910 | Specific Loss | - | 0.077449 | 0.800 Pa | 183.384 Pa
| 391848 | Specific Loss | - | 14.5216 | 150.000 Pa
| 407929 | Specific Loss | - | 2.9043 | 30.000 Pa
| 407949 | Specific Loss | - | 0.077449 | 0.800 Pa
| 407952 | Specific Loss | - | 0.077449 | 0.800 Pa
| 2216971 | Coefficient from ASHRAE Table | ED5-3 | 0 | 0.000 Pa
| 2631037 | Coefficient from ASHRAE Table | - | 0 | 0.000 Pa
| 2631039 | Coefficient from ASHRAE Table | ED4-1 | 0.095235 | 0.984 Pa
120 | 2631039 | Coefficient from ASHRAE Table | ED4-1 | 0 | 0.000 Pa | 1.052 Pa
| 2631045 | Coefficient from ASHRAE Table | - | 0 | 0.000 Pa
| 2631062 | Coefficient from ASHRAE Table | ED4-2 | 0.24864 | 1.052 Pa
| 2631065 | Coefficient from ASHRAE Table | - | 0 | 0.000 Pa
121 | 2631062 | Coefficient from ASHRAE Table | ED4-2 | 0 | 0.000 Pa | -0.800 Pa
| 2174871 | Coefficient from ASHRAE Table | ER5-1 | -0.69 | -0.800 Pa
122 | 2174871 | Coefficient from ASHRAE Table | ER5-1 | 0 | 0.000 Pa | 2.226 Pa
| 1565306 | Coefficient from ASHRAE Table | ER4-1 | 0.039355 | 0.325 Pa
| 1565318 | Coefficient from ASHRAE Table | CR3-1 | 0.11692 | 0.964 Pa
| 1565337 | Coefficient from ASHRAE Table | CR3-1 | 0.11358 | 0.937 Pa
123 | 1565300 | Coefficient from ASHRAE Table | - | 0 | 0.000 Pa | 0.000 Pa
| 1565306 | Coefficient from ASHRAE Table | ER4-1 | 0 | 0.000 Pa
124 | 2174664 | Coefficient from ASHRAE Table | SR5-11 | 0 | 0.000 Pa | 0.000 Pa
| 1565300 | Coefficient from ASHRAE Table | - | 0 | 0.000 Pa
125 | 2174664 | Coefficient from ASHRAE Table | SR5-11 | 0 | 0.000 Pa | 0.000 Pa
| 1619195 | Coefficient from ASHRAE Table | - | 0 | 0.000 Pa
126 | 1602962 | Coefficient from ASHRAE Table | - | 0 | 0.000 Pa | 0.000 Pa
| 1619195 | Coefficient from ASHRAE Table | - | 0 | 0.000 Pa
127 | 1602962 | Coefficient from ASHRAE Table | - | 0 | 0.000 Pa | 13.765 Pa
| 1603048 | Coefficient from ASHRAE Table | ER3-1 | 1.2014 | 13.765 Pa
| 1603143 | Coefficient from ASHRAE Table | - | 0 | 0.000 Pa
128 | 1603143 | Coefficient from ASHRAE Table | - | 0 | 0.000 Pa | 0.000 Pa
| 1603617 | Coefficient from ASHRAE Table | - | 0 | 0.000 Pa
129 | 1603617 | Coefficient from ASHRAE Table | - | 0 | 0.000 Pa | 8.684 Pa
| 1619171 | Coefficient from ASHRAE Table | ER3-1 | 1.1843 | 8.684 Pa
| 1620017 | Coefficient from ASHRAE Table | - | 0 | 0.000 Pa
130 | 1620017 | Coefficient from ASHRAE Table | - | 0 | 0.000 Pa | 0.000 Pa
| 2174598 | Coefficient from ASHRAE Table | SR5-11 | 0 | 0.000 Pa
131 | 2174598 | Coefficient from ASHRAE Table | SR5-11 | 0 | 0.000 Pa | 24.441 Pa
| 1620028 | Coefficient from ASHRAE Table | CR3-17 | 0.43768 | 3.610 Pa
| 1620031 | Coefficient from ASHRAE Table | CR3-17 | 0.43768 | 3.610 Pa
| 1620043 | Coefficient from ASHRAE Table | CR3-17 | 0.43768 | 3.610 Pa
| 1620994 | Coefficient from ASHRAE Table | CR3-17 | 0.43768 | 3.610 Pa
| 1671050 | Coefficient from ASHRAE Table | CR6-3 | 0 | 0.000 Pa
| 1671051 | Specific Loss | - | 1.2124 | 10.000 Pa
| 2440977 | Coefficient from ASHRAE Table | - | 0 | 0.000 Pa
132 | 1635842 | Coefficient from ASHRAE Table | - | 0 | 0.000 Pa | 0.000 Pa
| 2440977 | Coefficient from ASHRAE Table | - | 0 | 0.000 Pa
133 | 1588133 | Coefficient from ASHRAE Table | ER4-2 | 0.29491 | 2.334 Pa | 11.437 Pa
| 1635838 | Coefficient from ASHRAE Table | ER3-1 | 1.15 | 9.102 Pa
| 1635842 | Coefficient from ASHRAE Table | - | 0 | 0.000 Pa
134 | 1588133 | Coefficient from ASHRAE Table | ER4-2 | 0 | 0.000 Pa | 0.000 Pa
| 2177056 | Coefficient from ASHRAE Table | SR5-11 | 0 | 0.000 Pa
135 | 1607250 | Specific Loss | - | 0.30979 | 0.800 Pa | 184.982 Pa
| 1607255 | Specific Loss | - | 0.30979 | 0.800 Pa
| 1607276 | Specific Loss | - | 58.0866 | 150.000 Pa
| 1607277 | Specific Loss | - | 11.6173 | 30.000 Pa
| 2215575 | Specific Loss | - | 0.30979 | 0.800 Pa
| 2215600 | Coefficient from ASHRAE Table | ED5-3 | 1 | 2.582 Pa
136 | 1617964 | Coefficient from ASHRAE Table | ED4-2 | 0.16577 | 1.189 Pa | 1.989 Pa
| 2215573 | Specific Loss | - | 0.11153 | 0.800 Pa
| 2215600 | Coefficient from ASHRAE Table | ED5-3 | 0 | 0.000 Pa
137 | 1617964 | Coefficient from ASHRAE Table | ED4-2 | 0 | 0.000 Pa | 0.000 Pa
| 2177732 | Coefficient from ASHRAE Table | SR5-11 | 0 | 0.000 Pa
138 | 461510 | Specific Loss | - | 130.6948 | 150.000 Pa | 180.800 Pa
| 461511 | Specific Loss | - | 26.139 | 30.000 Pa
| 461512 | Specific Loss | - | 0.69704 | 0.800 Pa
| 2175093 | Coefficient from ASHRAE Table | SR5-11 | 0 | 0.000 Pa
139 | 2175093 | Coefficient from ASHRAE Table | SR5-11 | 0 | 0.000 Pa | 0.000 Pa
| 2175034 | Coefficient from ASHRAE Table | SR5-11 | 0 | 0.000 Pa
140 | 2175034 | Coefficient from ASHRAE Table | SR5-11 | 0 | 0.000 Pa | 0.000 Pa
| 2174962 | Coefficient from ASHRAE Table | SR5-11 | 0 | 0.000 Pa
141 | 2174962 | Coefficient from ASHRAE Table | SR5-11 | 0 | 0.000 Pa | 0.000 Pa
| 1588961 | Coefficient from ASHRAE Table | - | 0 | 0.000 Pa
142 | 1588935 | Coefficient from ASHRAE Table | ER4-2 | 0.14559 | 1.055 Pa | 9.392 Pa
| 1588955 | Coefficient from ASHRAE Table | ER3-1 | 1.15 | 8.337 Pa
| 1588961 | Coefficient from ASHRAE Table | - | 0 | 0.000 Pa
143 | 1588929 | Coefficient from ASHRAE Table | ER4-2 | 0.15362 | 0.456 Pa | 30.456 Pa
| 1588934 | Specific Loss | - | 10.103 | 30.000 Pa
| 1588935 | Coefficient from ASHRAE Table | ER4-2 | 0 | 0.000 Pa
144 | 1565395 | Coefficient from ASHRAE Table | - | 0 | 0.000 Pa | 150.721 Pa
| 1588921 | Coefficient from ASHRAE Table | CR3-1 | 0.099515 | 0.721 Pa
| 1588925 | Specific Loss | - | 20.6909 | 150.000 Pa
| 1588929 | Coefficient from ASHRAE Table | ER4-2 | 0 | 0.000 Pa
145 | 1565381 | Coefficient from ASHRAE Table | CR3-1 | 0.068706 | 0.498 Pa | 5.518 Pa
| 1565386 | Coefficient from ASHRAE Table | CR3-1 | 0.068706 | 0.498 Pa
| 1565390 | Coefficient from ASHRAE Table | CR3-1 | 0.099515 | 0.721 Pa
| 1565395 | Coefficient from ASHRAE Table | - | 0 | 0.000 Pa
| 2174871 | Coefficient from ASHRAE Table | ER5-1 | 0.52417 | 3.800 Pa
146 | 461426 | Specific Loss | - | 130.6948 | 150.000 Pa | 180.800 Pa
| 461427 | Specific Loss | - | 26.139 | 30.000 Pa
| 461428 | Specific Loss | - | 0.69704 | 0.800 Pa
| 2175146 | Coefficient from ASHRAE Table | SR5-11 | 0 | 0.000 Pa
147 | 2175146 | Coefficient from ASHRAE Table | SR5-11 | 0 | 0.000 Pa | 0.000 Pa
| 2175093 | Coefficient from ASHRAE Table | SR5-11 | 0 | 0.000 Pa
148 | 461406 | Specific Loss | - | 0.69704 | 0.800 Pa | 181.788 Pa
| 461416 | Specific Loss | - | 26.139 | 30.000 Pa
| 461417 | Specific Loss | - | 130.6948 | 150.000 Pa
| 461420 | Coefficient from ASHRAE Table | ED4-2 | 0.16417 | 0.188 Pa
| 461421 | Specific Loss | - | 0.69704 | 0.800 Pa
149 | 461420 | Coefficient from ASHRAE Table | ED4-2 | 0 | 0.000 Pa | 0.000 Pa
| 2175146 | Coefficient from ASHRAE Table | SR5-11 | 0 | 0.000 Pa
150 | 1746736 | Coefficient from ASHRAE Table | ED5-4 | 1.5956 | 6.751 Pa | 6.751 Pa
151 | 1714024 | Specific Loss | - | 0.11541 | 0.800 Pa | 191.947 Pa
| 1746736 | Coefficient from ASHRAE Table | ED5-4 | 0 | 0.000 Pa
| 1746755 | Specific Loss | - | 0.11541 | 0.800 Pa
| 1746758 | Specific Loss | - | 4.3278 | 30.000 Pa
| 1746759 | Specific Loss | - | 21.6389 | 150.000 Pa
| 2639590 | Coefficient from ASHRAE Table | ED5-3 | 1.4927 | 10.347 Pa
152 | 1714021 | Specific Loss | - | 0.072437 | 0.800 Pa | 3.852 Pa
| 1746984 | Coefficient from ASHRAE Table | - | 0 | 0.000 Pa
| 1746990 | Coefficient from ASHRAE Table | ED5-3 | 0.20392 | 2.252 Pa
| 1775830 | Specific Loss | - | 0.072437 | 0.800 Pa
| 2639590 | Coefficient from ASHRAE Table | ED5-3 | 0 | 0.000 Pa
153 | 1714030 | Specific Loss | - | 0.049433 | 0.800 Pa | 1.871 Pa
| 1746990 | Coefficient from ASHRAE Table | ED5-3 | 0 | 0.000 Pa
| 2639372 | Coefficient from ASHRAE Table | ED5-3 | 0.066201 | 1.071 Pa
154 | 1713949 | Specific Loss | - | 0.038683 | 0.800 Pa | 1.600 Pa
| 1775840 | Specific Loss | - | 0.038683 | 0.800 Pa
| 1775843 | Coefficient from ASHRAE Table | - | 0 | 0.000 Pa
| 2176432 | Coefficient from ASHRAE Table | SR5-11 | 0 | 0.000 Pa
| 2639372 | Coefficient from ASHRAE Table | ED5-3 | 0 | 0.000 Pa
155 | 1746736 | Coefficient from ASHRAE Table | ED5-4 | 1.5956 | 6.751 Pa | 6.751 Pa
156 | 1601734 | Coefficient from ASHRAE Table | - | 0 | 0.000 Pa | 3.111 Pa
| 1601747 | Specific Loss | - | 0.66475 | 0.800 Pa
| 1601751 | Coefficient from ASHRAE Table | - | 0 | 0.000 Pa
| 2213548 | Coefficient from ASHRAE Table | ED5-3 | 1.92 | 2.311 Pa
157 | 1237415 | Specific Loss | - | 0.16619 | 0.800 Pa | 184.000 Pa
| 1589300 | Coefficient from ASHRAE Table | CD3-11 | 0 | 0.000 Pa
| 1589302 | Specific Loss | - | 0.16619 | 0.800 Pa
| 1589339 | Specific Loss | - | 0.16619 | 0.800 Pa
| 1601614 | Specific Loss | - | 31.1601 | 150.000 Pa
| 1601615 | Specific Loss | - | 6.232 | 30.000 Pa
| 1601617 | Specific Loss | - | 0.16619 | 0.800 Pa
| 1601621 | Coefficient from ASHRAE Table | - | 0 | 0.000 Pa
| 1601638 | Coefficient from ASHRAE Table | - | 0 | 0.000 Pa
| 1601657 | Coefficient from ASHRAE Table | - | 0 | 0.000 Pa
| 2177371 | Coefficient from ASHRAE Table | SR5-11 | 0 | 0.000 Pa
| 2213513 | Specific Loss | - | 0.16619 | 0.800 Pa
| 2213548 | Coefficient from ASHRAE Table | ED5-3 | 0 | 0.000 Pa
158 | 1601768 | Coefficient from ASHRAE Table | - | 0 | 0.000 Pa | 2.022 Pa
| 2213548 | Coefficient from ASHRAE Table | ED5-3 | 1.68 | 2.022 Pa
159 | 1722582 | Coefficient from ASHRAE Table | ED5-3 | 1.92 | 3.443 Pa | 4.243 Pa
| 1722596 | Specific Loss | - | 0.4461 | 0.800 Pa
| 1722599 | Coefficient from ASHRAE Table | - | 0 | 0.000 Pa
160 | 1713704 | Coefficient from ASHRAE Table | ED4-1 | 0.38104 | 2.733 Pa | 184.333 Pa
| 1713850 | Specific Loss | - | 0.11153 | 0.800 Pa
| 1713853 | Specific Loss | - | 0.11153 | 0.800 Pa
| 1722579 | Specific Loss | - | 4.1822 | 30.000 Pa
| 1722580 | Specific Loss | - | 20.9112 | 150.000 Pa
| 1722582 | Coefficient from ASHRAE Table | ED5-3 | 0 | 0.000 Pa
161 | 1713704 | Coefficient from ASHRAE Table | ED4-1 | 0 | 0.000 Pa | 0.922 Pa
| 2214633 | Coefficient from ASHRAE Table | ED5-3 | 0.76641 | 0.922 Pa
162 | 1722582 | Coefficient from ASHRAE Table | ED5-3 | 1.68 | 3.013 Pa | 3.013 Pa
163 | 1784949 | Coefficient from ASHRAE Table | ED5-3 | -9.1124 | -10.458 Pa | 171.142 Pa
| 1784951 | Specific Loss | - | 0.69704 | 0.800 Pa
| 1784953 | Specific Loss | - | 130.6948 | 150.000 Pa
| 1784954 | Specific Loss | - | 26.139 | 30.000 Pa
| 1784955 | Specific Loss | - | 0.69704 | 0.800 Pa
164 | 1803431 | Specific Loss | - | 0.30979 | 0.800 Pa | 182.400 Pa
| 1803433 | Specific Loss | - | 0.30979 | 0.800 Pa
| 1803470 | Specific Loss | - | 58.0866 | 150.000 Pa
| 1803471 | Specific Loss | - | 11.6173 | 30.000 Pa
| 1803472 | Specific Loss | - | 0.30979 | 0.800 Pa
| 2178743 | Coefficient from ASHRAE Table | SR5-11 | 0 | 0.000 Pa
165 | 1803425 | Specific Loss | - | 0.30979 | 0.800 Pa | 184.000 Pa
| 1803427 | Specific Loss | - | 0.30979 | 0.800 Pa
| 1803462 | Coefficient from ASHRAE Table | - | 0 | 0.000 Pa
| 1803464 | Coefficient from ASHRAE Table | - | 0 | 0.000 Pa
| 1803476 | Specific Loss | - | 58.0866 | 150.000 Pa
| 1803477 | Specific Loss | - | 11.6173 | 30.000 Pa
| 1803478 | Specific Loss | - | 0.30979 | 0.800 Pa
| 1803483 | Specific Loss | - | 0.30979 | 0.800 Pa
| 1803485 | Specific Loss | - | 0.30979 | 0.800 Pa
| 2178792 | Coefficient from ASHRAE Table | SR5-11 | 0 | 0.000 Pa
166 | 1784763 | Coefficient from ASHRAE Table | ED5-3 | -4.0791 | -4.682 Pa | 176.918 Pa
| 1784767 | Specific Loss | - | 0.69704 | 0.800 Pa
| 1784770 | Specific Loss | - | 130.6948 | 150.000 Pa
| 1784771 | Specific Loss | - | 26.139 | 30.000 Pa
| 1784772 | Specific Loss | - | 0.69704 | 0.800 Pa
167 | 982849 | Specific Loss | - | 0.4461 | 0.800 Pa | 6.643 Pa
| 982854 | Coefficient from ASHRAE Table | - | 0 | 0.000 Pa
| 982860 | Specific Loss | - | 0.4461 | 0.800 Pa
| 982865 | Specific Loss | - | 0.4461 | 0.800 Pa
| 982868 | Specific Loss | - | 0.4461 | 0.800 Pa
| 982902 | Coefficient from ASHRAE Table | ED5-3 | 1.92 | 3.443 Pa
168 | 982902 | Coefficient from ASHRAE Table | ED5-3 | 0 | 0.000 Pa | 184.895 Pa
| 1589698 | Specific Loss | - | 0.11153 | 0.800 Pa
| 1589725 | Specific Loss | - | 20.9112 | 150.000 Pa
| 1589726 | Specific Loss | - | 4.1822 | 30.000 Pa
| 2234210 | Coefficient from ASHRAE Table | ED4-1 | 0.57088 | 4.095 Pa
169 | 2234210 | Coefficient from ASHRAE Table | ED4-1 | 0 | 0.000 Pa | 8.452 Pa
| 2235284 | Coefficient from ASHRAE Table | ED5-3 | 11.0507 | 8.452 Pa
170 | 1722631 | Specific Loss | - | 0.30979 | 0.800 Pa | 184.982 Pa
| 1722643 | Specific Loss | - | 0.30979 | 0.800 Pa
| 1722679 | Specific Loss | - | 11.6173 | 30.000 Pa
| 1722681 | Specific Loss | - | 58.0866 | 150.000 Pa
| 2216004 | Coefficient from ASHRAE Table | ED5-3 | 1 | 2.582 Pa
| 2236198 | Specific Loss | - | 0.30979 | 0.800 Pa
171 | 1722646 | Specific Loss | - | 0.11153 | 0.800 Pa | 1.992 Pa
| 1734131 | Coefficient from ASHRAE Table | ED4-2 | 0.16617 | 1.192 Pa
| 2216004 | Coefficient from ASHRAE Table | ED5-3 | 0 | 0.000 Pa
172 | 1734131 | Coefficient from ASHRAE Table | ED4-2 | 0 | 0.000 Pa | 0.000 Pa
| 2178390 | Coefficient from ASHRAE Table | SR5-11 | 0 | 0.000 Pa
173 | 2178390 | Coefficient from ASHRAE Table | SR5-11 | 0 | 0.000 Pa | 0.000 Pa
| 2178354 | Coefficient from ASHRAE Table | SR5-11 | 0 | 0.000 Pa
174 | 2178354 | Coefficient from ASHRAE Table | SR5-11 | 0 | 0.000 Pa | 0.000 Pa
| 2178316 | Coefficient from ASHRAE Table | SR5-11 | 0 | 0.000 Pa
175 | 2178316 | Coefficient from ASHRAE Table | SR5-11 | 0 | 0.000 Pa | 0.000 Pa
| 2178276 | Coefficient from ASHRAE Table | SR5-11 | 0 | 0.000 Pa
176 | 2178276 | Coefficient from ASHRAE Table | SR5-11 | 0 | 0.000 Pa | 15.773 Pa
| 1775434 | Coefficient from ASHRAE Table | ER3-1 | 1.15 | 14.090 Pa
| 1775445 | Coefficient from ASHRAE Table | CR3-1 | 0.068706 | 0.842 Pa
| 1775446 | Coefficient from ASHRAE Table | CR3-1 | 0.068706 | 0.842 Pa
| 1775450 | Coefficient from ASHRAE Table | - | 0 | 0.000 Pa
177 | 1775450 | Coefficient from ASHRAE Table | - | 0 | 0.000 Pa | 30.000 Pa
| 1775455 | Specific Loss | - | 5.9781 | 30.000 Pa
| 1775456 | Coefficient from ASHRAE Table | - | 0 | 0.000 Pa
178 | 1775456 | Coefficient from ASHRAE Table | - | 0 | 0.000 Pa | 150.000 Pa
| 1775462 | Specific Loss | - | 12.2431 | 150.000 Pa
| 1775476 | Coefficient from ASHRAE Table | - | 0 | 0.000 Pa
179 | 1775476 | Coefficient from ASHRAE Table | - | 0 | 0.000 Pa | 0.000 Pa
| 2178231 | Coefficient from ASHRAE Table | SR5-11 | 0 | 0.000 Pa
180 | 1722634 | Specific Loss | - | 0.69704 | 0.800 Pa | 184.623 Pa
| 1722637 | Specific Loss | - | 0.69704 | 0.800 Pa
| 1722682 | Specific Loss | - | 26.139 | 30.000 Pa
| 1722683 | Specific Loss | - | 130.6948 | 150.000 Pa
| 1722686 | Specific Loss | - | 0.69704 | 0.800 Pa
| 1722691 | Coefficient from ASHRAE Table | - | 0 | 0.000 Pa
| 1722694 | Specific Loss | - | 0.69704 | 0.800 Pa
| 2216004 | Coefficient from ASHRAE Table | ED5-3 | 1.24 | 1.423 Pa
181 | 1772604 | Specific Loss | - | 0.30979 | 0.800 Pa | 179.015 Pa
| 1775337 | Specific Loss | - | 0.30979 | 0.800 Pa
| 1775340 | Specific Loss | - | 0.30979 | 0.800 Pa
| 1775345 | Coefficient from ASHRAE Table | - | 0 | 0.000 Pa
| 1775385 | Specific Loss | - | 58.0866 | 150.000 Pa
| 1775386 | Specific Loss | - | 11.6173 | 30.000 Pa
| 1775391 | Specific Loss | - | 0.30979 | 0.800 Pa
| 1775394 | Specific Loss | - | 0.30979 | 0.800 Pa
| 1775396 | Coefficient from ASHRAE Table | - | 0 | 0.000 Pa
| 1784713 | Coefficient from ASHRAE Table | - | 0 | 0.000 Pa
| 2236143 | Coefficient from ASHRAE Table | ED5-3 | -1.9304 | -4.985 Pa
182 | 1803624 | Coefficient from ASHRAE Table | - | 0 | 0.000 Pa | 0.331 Pa
| 1803637 | Coefficient from ASHRAE Table | ED4-1 | 0.1125 | 0.331 Pa
183 | 1803502 | Specific Loss | - | 0.11153 | 0.800 Pa | 181.600 Pa
| 1803504 | Specific Loss | - | 0.11153 | 0.800 Pa
| 1803622 | Specific Loss | - | 20.9112 | 150.000 Pa
| 1803623 | Specific Loss | - | 4.1822 | 30.000 Pa
| 1803637 | Coefficient from ASHRAE Table | ED4-1 | 0 | 0.000 Pa
| 2178604 | Coefficient from ASHRAE Table | SR5-11 | 0 | 0.000 Pa
184 | 1793033 | Specific Loss | - | 0.46163 | 0.800 Pa | 185.699 Pa
| 1793037 | Specific Loss | - | 0.46163 | 0.800 Pa
| 1793320 | Specific Loss | - | 0.46163 | 0.800 Pa
| 1793380 | Specific Loss | - | 0.46163 | 0.800 Pa
| 1793388 | Specific Loss | - | 0.46163 | 0.800 Pa
| 1793392 | Specific Loss | - | 0.46163 | 0.800 Pa
| 1794247 | Specific Loss | - | 0.46163 | 0.800 Pa
| 1794332 | Coefficient from ASHRAE Table | - | 0 | 0.000 Pa
| 1794403 | Specific Loss | - | 17.3111 | 30.000 Pa
| 1794444 | Specific Loss | - | 86.5557 | 150.000 Pa
| 1794489 | Coefficient from ASHRAE Table | - | 0 | 0.000 Pa
| 2178171 | Coefficient from ASHRAE Table | - | 0 | 0.000 Pa
| 2178173 | Coefficient from ASHRAE Table | CD3-11 | 0.057192 | 0.099 Pa
185 | 1237397 | Specific Loss | - | 0.66475 | 0.800 Pa | 185.600 Pa
| 1237407 | Specific Loss | - | 0.66475 | 0.800 Pa
| 1722415 | Specific Loss | - | 0.66475 | 0.800 Pa
| 1722417 | Specific Loss | - | 0.66475 | 0.800 Pa
| 1722421 | Coefficient from ASHRAE Table | - | 0 | 0.000 Pa
| 1722424 | Specific Loss | - | 0.66475 | 0.800 Pa
| 1722427 | Specific Loss | - | 0.66475 | 0.800 Pa
| 1722430 | Specific Loss | - | 124.6402 | 150.000 Pa
| 1722431 | Specific Loss | - | 24.928 | 30.000 Pa
| 1722544 | Coefficient from ASHRAE Table | CD3-11 | 0 | 0.000 Pa
| 1722546 | Specific Loss | - | 0.66475 | 0.800 Pa
| 2178046 | Coefficient from ASHRAE Table | - | 0 | 0.000 Pa
186 | 1562593 | Coefficient from ASHRAE Table | - | 0 | 0.000 Pa | -0.137 Pa
| 2215371 | Coefficient from ASHRAE Table | ED5-3 | -0.1 | -0.137 Pa
187 | 1562572 | Coefficient from ASHRAE Table | - | 0 | 0.000 Pa | 2.299 Pa
| 2215170 | Coefficient from ASHRAE Table | ED5-3 | 1.68 | 2.299 Pa
188 | 1746806 | Specific Loss | - | 0.2276 | 0.800 Pa | 9.149 Pa
| 1746813 | Coefficient from ASHRAE Table | ED5-3 | 1.92 | 6.749 Pa
| 1775878 | Specific Loss | - | 0.2276 | 0.800 Pa
| 1775884 | Coefficient from ASHRAE Table | - | 0 | 0.000 Pa
| 2214968 | Specific Loss | - | 0.2276 | 0.800 Pa
189 | 1713982 | Specific Loss | - | 0.056901 | 0.800 Pa | 191.744 Pa
| 1713984 | Specific Loss | - | 0.056901 | 0.800 Pa
| 1713988 | Specific Loss | - | 0.056901 | 0.800 Pa
| 1713994 | Specific Loss | - | 0.056901 | 0.800 Pa
| 1746760 | Specific Loss | - | 0.056901 | 0.800 Pa
| 1746763 | Coefficient from ASHRAE Table | - | 0 | 0.000 Pa
| 1746766 | Coefficient from ASHRAE Table | ED4-1 | 0.43697 | 6.144 Pa
| 1746786 | Coefficient from ASHRAE Table | - | 0 | 0.000 Pa
| 1746789 | Specific Loss | - | 0.056901 | 0.800 Pa
| 1746798 | Coefficient from ASHRAE Table | - | 0 | 0.000 Pa
| 1746813 | Coefficient from ASHRAE Table | ED5-3 | 0 | 0.000 Pa
| 1747068 | Coefficient from ASHRAE Table | - | 0 | 0.000 Pa
| 1747116 | Specific Loss | - | 0.056901 | 0.800 Pa
| 1747488 | Coefficient from ASHRAE Table | - | 0 | 0.000 Pa
| 1749670 | Specific Loss | - | 2.1338 | 30.000 Pa
| 1749743 | Specific Loss | - | 10.669 | 150.000 Pa
190 | 1746766 | Coefficient from ASHRAE Table | ED4-1 | 0 | 0.000 Pa | 9.805 Pa
| 1746782 | Coefficient from ASHRAE Table | - | 0 | 0.000 Pa
| 2639590 | Coefficient from ASHRAE Table | ED5-3 | 6.5406 | 9.805 Pa
191 | 1746813 | Coefficient from ASHRAE Table | ED5-3 | 1.68 | 5.905 Pa | 7.505 Pa
| 1746817 | Specific Loss | - | 0.2276 | 0.800 Pa
| 1775881 | Specific Loss | - | 0.2276 | 0.800 Pa
| 1775887 | Coefficient from ASHRAE Table | - | 0 | 0.000 Pa
192 | 1514348 | Specific Loss | - | 0.25967 | 0.800 Pa | 187.576 Pa
| 1514353 | Specific Loss | - | 0.25967 | 0.800 Pa
| 1772480 | Coefficient from ASHRAE Table | - | 0 | 0.000 Pa
| 1772486 | Coefficient from ASHRAE Table | - | 0 | 0.000 Pa
| 1772490 | Specific Loss | - | 48.6876 | 150.000 Pa
| 1772491 | Specific Loss | - | 9.7375 | 30.000 Pa
| 1772492 | Coefficient from ASHRAE Table | - | 0 | 0.000 Pa
| 1772498 | Specific Loss | - | 0.25967 | 0.800 Pa
| 2640058 | Coefficient from ASHRAE Table | ED5-3 | 1.68 | 5.176 Pa
193 | 1722658 | Specific Loss | - | 0.69704 | 0.800 Pa | 180.800 Pa
| 1734150 | Specific Loss | - | 26.139 | 30.000 Pa
| 1734151 | Specific Loss | - | 130.6948 | 150.000 Pa
| 2178354 | Coefficient from ASHRAE Table | SR5-11 | 0 | 0.000 Pa
194 | 1722673 | Specific Loss | - | 0.69704 | 0.800 Pa | 180.800 Pa
| 1734176 | Specific Loss | - | 26.139 | 30.000 Pa
| 1734177 | Specific Loss | - | 130.6948 | 150.000 Pa
| 2178276 | Coefficient from ASHRAE Table | SR5-11 | 0 | 0.000 Pa
195 | 1722664 | Specific Loss | - | 0.69704 | 0.800 Pa | 180.800 Pa
| 1734163 | Specific Loss | - | 26.139 | 30.000 Pa
| 1734164 | Specific Loss | - | 130.6948 | 150.000 Pa
| 2178316 | Coefficient from ASHRAE Table | SR5-11 | 0 | 0.000 Pa
196 | 1722652 | Specific Loss | - | 0.69704 | 0.800 Pa | 180.800 Pa
| 1734127 | Specific Loss | - | 26.139 | 30.000 Pa
| 1734128 | Specific Loss | - | 130.6948 | 150.000 Pa
| 2178390 | Coefficient from ASHRAE Table | SR5-11 | 0 | 0.000 Pa
197 | 407936 | Specific Loss | - | 0.30979 | 0.800 Pa | 5.938 Pa
| 2216971 | Coefficient from ASHRAE Table | ED5-3 | 1.68 | 4.338 Pa
| 2216980 | Specific Loss | - | 0.30979 | 0.800 Pa
198 | 1565165 | Specific Loss | - | 124.6402 | 150.000 Pa | 183.622 Pa
| 1565166 | Specific Loss | - | 24.928 | 30.000 Pa
| 2235692 | Coefficient from ASHRAE Table | ED5-3 | 1.68 | 2.022 Pa
| 2235704 | Specific Loss | - | 0.66475 | 0.800 Pa
| 2235706 | Specific Loss | - | 0.66475 | 0.800 Pa
199 | 1565168 | Coefficient from ASHRAE Table | - | 0 | 0.000 Pa | 0.000 Pa
| 2174598 | Coefficient from ASHRAE Table | SR5-11 | 0 | 0.000 Pa
| 2235692 | Coefficient from ASHRAE Table | ED5-3 | 0 | 0.000 Pa
200 | 1714012 | Specific Loss | - | 0.17426 | 0.800 Pa | 180.800 Pa
| 1714014 | Specific Loss | - | 0.17426 | 0.800 Pa
| 1714018 | Specific Loss | - | 0.17426 | 0.800 Pa
| 1746990 | Coefficient from ASHRAE Table | ED5-3 | -1.2199 | -5.600 Pa
| 1747625 | Specific Loss | - | 0.17426 | 0.800 Pa
| 1747701 | Specific Loss | - | 0.17426 | 0.800 Pa
| 1747734 | Coefficient from ASHRAE Table | - | 0 | 0.000 Pa
| 1747788 | Specific Loss | - | 0.17426 | 0.800 Pa
| 1749996 | Specific Loss | - | 6.5347 | 30.000 Pa
| 1784624 | Specific Loss | - | 32.6737 | 150.000 Pa
| 1784628 | Specific Loss | - | 0.17426 | 0.800 Pa
| 1784633 | Coefficient from ASHRAE Table | - | 0 | 0.000 Pa
| 1784636 | Specific Loss | - | 0.17426 | 0.800 Pa
201 | 1565137 | Specific Loss | - | 124.6402 | 150.000 Pa | 183.911 Pa
| 1565138 | Specific Loss | - | 24.928 | 30.000 Pa
| 1565145 | Specific Loss | - | 0.66475 | 0.800 Pa
| 1565148 | Coefficient from ASHRAE Table | - | 0 | 0.000 Pa
| 2235647 | Specific Loss | - | 0.66475 | 0.800 Pa
| 2235692 | Coefficient from ASHRAE Table | ED5-3 | 1.92 | 2.311 Pa
202 | 982880 | Specific Loss | - | 0.4461 | 0.800 Pa | 5.413 Pa
| 982885 | Specific Loss | - | 0.4461 | 0.800 Pa
| 982887 | Specific Loss | - | 0.4461 | 0.800 Pa
| 982893 | Coefficient from ASHRAE Table | - | 0 | 0.000 Pa
| 982902 | Coefficient from ASHRAE Table | ED5-3 | 1.68 | 3.013 Pa
203 | 1631370 | Specific Loss | - | 0.13892 | 0.800 Pa | 2.248 Pa
| 1631373 | Specific Loss | - | 0.13892 | 0.800 Pa
| 1631376 | Coefficient from ASHRAE Table | ED4-1 | 0.1125 | 0.648 Pa
| 1631378 | Coefficient from ASHRAE Table | - | 0 | 0.000 Pa
204 | 1631376 | Coefficient from ASHRAE Table | ED4-1 | 0 | 0.000 Pa | 180.800 Pa
| 1631382 | Specific Loss | - | 2.1338 | 30.000 Pa
| 1631383 | Specific Loss | - | 10.669 | 150.000 Pa
| 2175314 | Coefficient from ASHRAE Table | SR5-11 | 0 | 0.000 Pa
| 2175407 | Specific Loss | - | 0.056901 | 0.800 Pa
| 2175409 | Coefficient from ASHRAE Table | CD3-11 | 0 | 0.000 Pa
205 | 461520 | Specific Loss | - | 130.6948 | 150.000 Pa | 180.800 Pa
| 461521 | Specific Loss | - | 26.139 | 30.000 Pa
| 461522 | Specific Loss | - | 0.69704 | 0.800 Pa
| 2174962 | Coefficient from ASHRAE Table | SR5-11 | 0 | 0.000 Pa
206 | 1713931 | Specific Loss | - | 0.30979 | 0.800 Pa | 174.146 Pa
| 1713937 | Specific Loss | - | 0.30979 | 0.800 Pa
| 1749359 | Specific Loss | - | 11.6173 | 30.000 Pa
| 1749411 | Specific Loss | - | 58.0866 | 150.000 Pa
| 1775822 | Specific Loss | - | 0.30979 | 0.800 Pa
| 1775825 | Coefficient from ASHRAE Table | - | 0 | 0.000 Pa
| 1775833 | Coefficient from ASHRAE Table | - | 0 | 0.000 Pa
| 1775861 | Specific Loss | - | 0.30979 | 0.800 Pa
| 1775864 | Specific Loss | - | 0.30979 | 0.800 Pa
| 1775867 | Coefficient from ASHRAE Table | - | 0 | 0.000 Pa
| 2639372 | Coefficient from ASHRAE Table | ED5-3 | -3.8158 | -9.854 Pa
207 | 461534 | Coefficient from ASHRAE Table | ED4-1 | 0.1125 | 0.195 Pa | 0.195 Pa
208 | 461528 | Coefficient from ASHRAE Table | - | 0 | 0.000 Pa | 181.600 Pa
| 461531 | Specific Loss | - | 0.18908 | 0.800 Pa
| 461534 | Coefficient from ASHRAE Table | ED4-1 | 0 | 0.000 Pa
| 461538 | Specific Loss | - | 35.4532 | 150.000 Pa
| 461539 | Specific Loss | - | 7.0906 | 30.000 Pa
| 461542 | Specific Loss | - | 0.18908 | 0.800 Pa
| 1684853 | Coefficient from ASHRAE Table | CD3-11 | 0 | 0.000 Pa
| 2174664 | Coefficient from ASHRAE Table | SR5-11 | 0 | 0.000 Pa
209 | 1806384 | Specific Loss | - | 10.2105 | 30.000 Pa | 182.400 Pa
| 1806429 | Coefficient from ASHRAE Table | - | 0 | 0.000 Pa
| 1806434 | Specific Loss | - | 0.27228 | 0.800 Pa
| 1806437 | Specific Loss | - | 51.0526 | 150.000 Pa
| 1806438 | Coefficient from ASHRAE Table | - | 0 | 0.000 Pa
| 1806447 | Specific Loss | - | 0.27228 | 0.800 Pa
| 1806450 | Coefficient from ASHRAE Table | CD3-11 | 0 | 0.000 Pa
| 1806456 | Specific Loss | - | 0.27228 | 0.800 Pa
| 2176394 | Coefficient from ASHRAE Table | SR5-11 | 0 | 0.000 Pa
210 | 461515 | Specific Loss | - | 130.6948 | 150.000 Pa | 180.800 Pa
| 461516 | Specific Loss | - | 26.139 | 30.000 Pa
| 461517 | Specific Loss | - | 0.69704 | 0.800 Pa
| 2175034 | Coefficient from ASHRAE Table | SR5-11 | 0 | 0.000 Pa
211 | 1607258 | Specific Loss | - | 0.69704 | 0.800 Pa | 184.623 Pa
| 1607261 | Coefficient from ASHRAE Table | - | 0 | 0.000 Pa
| 1607264 | Specific Loss | - | 0.69704 | 0.800 Pa
| 1607267 | Specific Loss | - | 0.69704 | 0.800 Pa
| 1607269 | Specific Loss | - | 0.69704 | 0.800 Pa
| 1607278 | Specific Loss | - | 130.6948 | 150.000 Pa
| 1607279 | Specific Loss | - | 26.139 | 30.000 Pa
| 2215600 | Coefficient from ASHRAE Table | ED5-3 | 1.24 | 1.423 Pa
212 | 1607291 | Specific Loss | - | 130.6948 | 150.000 Pa | 180.800 Pa
| 1607292 | Specific Loss | - | 26.139 | 30.000 Pa
| 1607293 | Specific Loss | - | 0.69704 | 0.800 Pa
| 2177695 | Coefficient from ASHRAE Table | SR5-11 | 0 | 0.000 Pa
213 | 1607301 | Specific Loss | - | 130.6948 | 150.000 Pa | 180.800 Pa
| 1607302 | Specific Loss | - | 26.139 | 30.000 Pa
| 1607322 | Specific Loss | - | 0.69704 | 0.800 Pa
| 2177658 | Coefficient from ASHRAE Table | SR5-11 | 0 | 0.000 Pa
214 | 1607309 | Specific Loss | - | 130.6948 | 150.000 Pa | 180.800 Pa
| 1607310 | Specific Loss | - | 26.139 | 30.000 Pa
| 1607317 | Specific Loss | - | 0.69704 | 0.800 Pa
| 2177599 | Coefficient from ASHRAE Table | SR5-11 | 0 | 0.000 Pa
215 | 1589019 | Specific Loss | - | 0.46163 | 0.800 Pa | 185.600 Pa
| 1589023 | Specific Loss | - | 0.46163 | 0.800 Pa
| 1589025 | Specific Loss | - | 0.46163 | 0.800 Pa
| 1589034 | Specific Loss | - | 0.46163 | 0.800 Pa
| 1589038 | Specific Loss | - | 0.46163 | 0.800 Pa
| 1589040 | Specific Loss | - | 0.46163 | 0.800 Pa
| 1589067 | Specific Loss | - | 0.46163 | 0.800 Pa
| 1589130 | Coefficient from ASHRAE Table | - | 0 | 0.000 Pa
| 1589185 | Specific Loss | - | 86.5557 | 150.000 Pa
| 1589186 | Specific Loss | - | 17.3111 | 30.000 Pa
| 1589246 | Coefficient from ASHRAE Table | CD3-11 | 0 | 0.000 Pa
| 2177388 | Coefficient from ASHRAE Table | SR5-11 | 0 | 0.000 Pa
216 | 1793377 | Specific Loss | - | 0.66475 | 0.800 Pa | 181.600 Pa
| 1806489 | Coefficient from ASHRAE Table | CD3-11 | 0 | 0.000 Pa
| 1806492 | Specific Loss | - | 124.6402 | 150.000 Pa
| 1806493 | Specific Loss | - | 24.928 | 30.000 Pa
| 1806494 | Specific Loss | - | 0.66475 | 0.800 Pa
| 2178004 | Coefficient from ASHRAE Table | SR5-11 | 0 | 0.000 Pa
L_Forluft 1
System Information
System Classification | Exhaust Air
System Type | Fortluft
System Name | L_Forluft 1
Abbreviation | L_Forluft
Total Pressure Loss Calculations by Sections
Section | Element | Flow | Size | Velocity | Velocity Pressure | Length | Loss Coefficient | Friction | Total Pressure Loss | Section Pressure Loss
1 | Duct | 4000.0 CMH | 1850 mmx1160 mm | 0.5 m/s | - | 379 | - | 0.00 Pa/m | 0.001 Pa | 0.140 Pa
| Fittings | 4000.0 CMH | - | 0.5 m/s | 0.161 Pa | - | 0.86249 | - | 0.139 Pa
| Equipment | 4000.0 CMH | - | - | - | - | - | - | 0.000 Pa
2 | Duct | 4000.0 CMH | 1000 mmx1000 mm | 1.1 m/s | - | 580 | - | 0.01 Pa/m | 0.008 Pa | 1.716 Pa
| Fittings | 4000.0 CMH | - | 1.1 m/s | 0.742 Pa | - | 2.3 | - | 1.707 Pa
3 | Duct | 4000.0 CMH | 1000 mmx1000 mm | 1.1 m/s | - | 9491 | - | 0.01 Pa/m | 0.138 Pa | 2.315 Pa
| Fittings | 4000.0 CMH | - | 1.1 m/s | 0.742 Pa | - | 2.932 | - | 2.177 Pa
| Air Terminal | 4000.0 CMH | - | - | - | - | - | - | 0.000 Pa
Critical Path : 1-2-3 ; Total Pressure Loss : 4.171 Pa
Detail Information of Straight Segment by Sections
Section | Element ID | Flow | Size | Velocity | Velocity Pressure | Length | Pressure Loss | Total Pressure Loss
1 | 2320370 | 4000.0 CMH | 1850 mmx1160 mm | 0.5 m/s | 0.161 Pa | 379 | 0.001 Pa | 0.001 Pa
2 | 191650 | 4000.0 CMH | 1000 mmx1000 mm | 1.1 m/s | 0.742 Pa | 380 | 0.006 Pa | 0.008 Pa
| 193312 | 4000.0 CMH | 1000 mmx1000 mm | 1.1 m/s | 0.742 Pa | 200 | 0.003 Pa
3 | 191668 | 4000.0 CMH | 1000 mmx1000 mm | 1.1 m/s | 0.742 Pa | 485 | 0.007 Pa | 0.138 Pa
| 191764 | 4000.0 CMH | 1000 mmx1000 mm | 1.1 m/s | 0.742 Pa | 353 | 0.005 Pa
| 191994 | 4000.0 CMH | 1000 mmx1000 mm | 1.1 m/s | 0.742 Pa | 1500 | 0.022 Pa
| 192494 | 4000.0 CMH | 1000 mmx1000 mm | 1.1 m/s | 0.742 Pa | 301 | 0.004 Pa
| 192640 | 4000.0 CMH | 1000 mmx1000 mm | 1.1 m/s | 0.742 Pa | 1084 | 0.016 Pa
| 192786 | 4000.0 CMH | 1000 mmx1000 mm | 1.1 m/s | 0.742 Pa | 734 | 0.011 Pa
| 192822 | 4000.0 CMH | 1000 mmx1000 mm | 1.1 m/s | 0.742 Pa | 734 | 0.011 Pa
| 193528 | 4000.0 CMH | 1000 mmx1000 mm | 1.1 m/s | 0.742 Pa | 1500 | 0.022 Pa
| 193874 | 4000.0 CMH | 1000 mmx1000 mm | 1.1 m/s | 0.742 Pa | 1474 | 0.021 Pa
| 923348 | 4000.0 CMH | 1000 mmx1000 mm | 1.1 m/s | 0.742 Pa | 1325 | 0.019 Pa
Fitting and Accessory Loss Coefficient Summary by Sections
Section | Element ID | Loss Method | ASHRAE Table | Loss Coefficient | Pressure Loss | Total Pressure Loss
1 | 1892155 | Coefficient from ASHRAE Table | ER4-2 | 0.86249 | 0.139 Pa | 0.139 Pa
2 | 1892150 | Coefficient from ASHRAE Table | ER3-1 | 1.15 | 0.854 Pa | 1.707 Pa
| 1892155 | Coefficient from ASHRAE Table | ER4-2 | 0 | 0.000 Pa
| 1892506 | Coefficient from ASHRAE Table | ER3-1 | 1.15 | 0.854 Pa
| 1892553 | Coefficient from ASHRAE Table | - | 0 | 0.000 Pa
3 | 819789 | Coefficient from ASHRAE Table | ER3-1 | 1.15 | 0.854 Pa | 2.177 Pa
| 819791 | Coefficient from ASHRAE Table | CR3-1 | 0.31602 | 0.235 Pa
| 819907 | Coefficient from ASHRAE Table | ER3-1 | 1.15 | 0.854 Pa
| 1892484 | Coefficient from ASHRAE Table | CR3-1 | 0.31602 | 0.235 Pa
| 1892553 | Coefficient from ASHRAE Table | - | 0 | 0.000 Pa