## Sheet1
Duct Pressure Loss Report
Project Name
Project Issue Date
Project Status
Client Name
Project Address
Project Number
Organization Name
Organization Description
Building Name
Author
IfcSite GUID | 06dWEt2jDAexxjgLznnrNn
IfcBuilding GUID | 06dWEt2jDAexxjgLznnrNo
IfcProject GUID | 06dWEt2jDAexxjgLznnrNp
Document GUID
SR Document GUID
PrintManagerSettings
SiteName
AreaCalculationInternationalOptions
ADSK_DICTIONARY_AREA_CALCULATION_TYPE
AreaCalculationInternationalBuildNumber
RoomBookInternationalBuildNumber
BuildingbookInternationalBuildNumber
Run Time | 3/3/2025 5:07:31 PM
L_Aussenluft 1
System Information
System Classification | Supply Air
System Type | Außenluft
System Name | L_Aussenluft 1
Abbreviation | L_Aussenluft
Total Pressure Loss Calculations by Sections
Section | Element | Flow | Size | Velocity | Velocity Pressure | Length | Loss Coefficient | Friction | Total Pressure Loss | Section Pressure Loss
1 | Duct | 4200.0 CMH | 2000 mmx2145 mm | 0.3 m/s | - | 95 | - | 0.00 Pa/m | 0.000 Pa | 20.000 Pa
| Fittings | 4200.0 CMH | - | 0.3 m/s | 0.044 Pa | - | 0 | - | 0.000 Pa
| Air Terminal | 4200.0 CMH | - | - | - | - | - | - | 20.000 Pa
2 | Duct | 4200.0 CMH | 1300 mmx1600 mm | 0.6 m/s | - | 2270 | - | 0.00 Pa/m | 0.006 Pa | 0.165 Pa
| Fittings | 4200.0 CMH | - | 0.6 m/s | 0.189 Pa | - | 0.83742 | - | 0.158 Pa
3 | Duct | 4200.0 CMH | 1300 mmx1600 mm | 0.6 m/s | - | 8992 | - | 0.00 Pa/m | 0.025 Pa | 0.426 Pa
| Fittings | 4200.0 CMH | - | 0.6 m/s | 0.189 Pa | - | 2.121 | - | 0.401 Pa
4 | Duct | 4200.0 CMH | 1850 mmx1160 mm | 0.5 m/s | - | 540 | - | 0.00 Pa/m | 0.001 Pa | 0.009 Pa
| Fittings | 4200.0 CMH | - | 0.5 m/s | 0.178 Pa | - | 0.041885 | - | 0.007 Pa
| Equipment | 4200.0 CMH | - | - | - | - | - | - | 0.000 Pa
Critical Path : 1-2-3-4 ; Total Pressure Loss : 20.600 Pa
Detail Information of Straight Segment by Sections
Section | Element ID | Flow | Size | Velocity | Velocity Pressure | Length | Pressure Loss | Total Pressure Loss
1 | 192302 | 4200.0 CMH | 2000 mmx2145 mm | 0.3 m/s | 0.044 Pa | 95 | 0.000 Pa | 0.000 Pa
2 | 193178 | 4200.0 CMH | 1300 mmx1600 mm | 0.6 m/s | 0.189 Pa | 515 | 0.001 Pa | 0.006 Pa
| 193786 | 4200.0 CMH | 1300 mmx1600 mm | 0.6 m/s | 0.189 Pa | 255 | 0.001 Pa
| 194256 | 4200.0 CMH | 1300 mmx1600 mm | 0.6 m/s | 0.189 Pa | 1500 | 0.004 Pa
3 | 191534 | 4200.0 CMH | 1300 mmx1600 mm | 0.6 m/s | 0.189 Pa | 854 | 0.002 Pa | 0.025 Pa
| 191568 | 4200.0 CMH | 1300 mmx1600 mm | 0.6 m/s | 0.189 Pa | 508 | 0.001 Pa
| 191592 | 4200.0 CMH | 1300 mmx1600 mm | 0.6 m/s | 0.189 Pa | 791 | 0.002 Pa
| 191712 | 4200.0 CMH | 1300 mmx1600 mm | 0.6 m/s | 0.189 Pa | 1500 | 0.004 Pa
| 191720 | 4200.0 CMH | 1300 mmx1600 mm | 0.6 m/s | 0.189 Pa | 1500 | 0.004 Pa
| 193834 | 4200.0 CMH | 1300 mmx1600 mm | 0.6 m/s | 0.189 Pa | 1500 | 0.004 Pa
| 193882 | 4200.0 CMH | 1300 mmx1600 mm | 0.6 m/s | 0.189 Pa | 639 | 0.002 Pa
| 193930 | 4200.0 CMH | 1300 mmx1600 mm | 0.6 m/s | 0.189 Pa | 700 | 0.002 Pa
| 193988 | 4200.0 CMH | 1300 mmx1600 mm | 0.6 m/s | 0.189 Pa | 1000 | 0.003 Pa
4 | 2641374 | 4200.0 CMH | 1850 mmx1160 mm | 0.5 m/s | 0.178 Pa | 540 | 0.001 Pa | 0.001 Pa
Fitting and Accessory Loss Coefficient Summary by Sections
Section | Element ID | Loss Method | ASHRAE Table | Loss Coefficient | Pressure Loss | Total Pressure Loss
1 | 1888547 | Coefficient from ASHRAE Table | SR4-2 | 0 | 0.000 Pa | 0.000 Pa
2 | 819785 | Coefficient from ASHRAE Table | CR3-1 | 0.049928 | 0.009 Pa | 0.158 Pa
| 819787 | Coefficient from ASHRAE Table | CR3-17 | 0.64616 | 0.122 Pa
| 1888547 | Coefficient from ASHRAE Table | SR4-2 | 0.14134 | 0.027 Pa
| 1888555 | Coefficient from ASHRAE Table | SR4-2 | 0 | 0.000 Pa
3 | 819781 | Coefficient from ASHRAE Table | CR3-1 | 0.49513 | 0.094 Pa | 0.401 Pa
| 819783 | Coefficient from ASHRAE Table | CR3-1 | 0.49513 | 0.094 Pa
| 820056 | Coefficient from ASHRAE Table | SR3-1 | 1.1308 | 0.214 Pa
| 1888555 | Coefficient from ASHRAE Table | SR4-2 | 0 | 0.000 Pa
| 1888576 | Coefficient from ASHRAE Table | SR4-2 | 0 | 0.000 Pa
4 | 1888576 | Coefficient from ASHRAE Table | SR4-2 | 0.041885 | 0.007 Pa | 0.007 Pa
L_Zuluft 1
System Information
System Classification | Supply Air
System Type | Zuluft
System Name | L_Zuluft 1
Abbreviation | L_Zuluft
Total Pressure Loss Calculations by Sections
Section | Element | Flow | Size | Velocity | Velocity Pressure | Length | Loss Coefficient | Friction | Total Pressure Loss | Section Pressure Loss
1 | Duct | 250.0 CMH | 250 mmø | 1.4 m/s | - | 112 | - | 0.13 Pa/m | 0.014 Pa | 5.309 Pa
| Fittings | 250.0 CMH | - | 1.4 m/s | 1.203 Pa | - | 4.4 | - | 5.295 Pa
| Air Terminal | 250.0 CMH | - | - | - | - | - | - | 0.000 Pa
2 | Duct | 500.0 CMH | 250 mmø | 2.8 m/s | - | 4559 | - | 0.44 Pa/m | 1.993 Pa | 75.630 Pa
| Fittings | 500.0 CMH | - | 2.8 m/s | 4.814 Pa | - | 15.2968 | - | 73.637 Pa
3 | Duct | 650.0 CMH | 250 mmø | 3.7 m/s | - | 6237 | - | 0.70 Pa/m | 4.379 Pa | 39.893 Pa
| Fittings | 650.0 CMH | - | 3.7 m/s | 8.135 Pa | - | 4.3653 | - | 35.514 Pa
4 | Duct | 2099.8 CMH | 400 mmx400 mm | 3.6 m/s | - | 424 | - | 0.38 Pa/m | 0.163 Pa | 0.163 Pa
| Fittings | 2099.8 CMH | - | 3.6 m/s | 7.991 Pa | - | 0 | - | 0.000 Pa
5 | Duct | 2099.8 CMH | 400 mmx400 mm | 3.6 m/s | - | 1188 | - | 0.38 Pa/m | 0.456 Pa | 0.966 Pa
| Fittings | 2099.8 CMH | - | 3.6 m/s | 7.991 Pa | - | 0.063835 | - | 0.510 Pa
6 | Duct | 2349.8 CMH | 400 mmx400 mm | 4.1 m/s | - | 6406 | - | 0.47 Pa/m | 3.016 Pa | 17.241 Pa
| Fittings | 2349.8 CMH | - | 4.1 m/s | 10.007 Pa | - | 1.4214 | - | 14.225 Pa
7 | Duct | 3299.8 CMH | 500 mmx500 mm | 3.7 m/s | - | 1919 | - | 0.29 Pa/m | 0.563 Pa | 0.909 Pa
| Fittings | 3299.8 CMH | - | 3.7 m/s | 8.083 Pa | - | 0.042778 | - | 0.346 Pa
8 | Duct | 3299.8 CMH | 600 mmx600 mm | 2.5 m/s | - | 1911 | - | 0.12 Pa/m | 0.231 Pa | 1.998 Pa
| Fittings | 3299.8 CMH | - | 2.5 m/s | 3.898 Pa | - | 0.45331 | - | 1.767 Pa
9 | Duct | 5399.6 CMH | 600 mmx600 mm | 4.2 m/s | - | 15421 | - | 0.30 Pa/m | 4.614 Pa | 45.025 Pa
| Fittings | 5399.6 CMH | - | 4.2 m/s | 10.438 Pa | - | 3.8715 | - | 40.410 Pa
10 | Duct | 12699.6 CMH | 1000 mmx1000 mm | 3.5 m/s | - | 23682 | - | 0.12 Pa/m | 2.813 Pa | 29.897 Pa
| Fittings | 12699.6 CMH | - | 3.5 m/s | 7.483 Pa | - | 3.6195 | - | 27.084 Pa
11 | Fittings | 12699.6 CMH | - | 0.0 m/s | 1.625 Pa | - | 0 | - | 0.000 Pa | 0.000 Pa
| Equipment | 12699.6 CMH | - | - | - | - | - | - | 0.000 Pa
12 | Duct | 250.0 CMH | 250 mmø | 1.4 m/s | - | 2651 | - | 0.13 Pa/m | 0.336 Pa | 6.431 Pa
| Fittings | 250.0 CMH | - | 1.4 m/s | 1.203 Pa | - | 5.0647 | - | 6.095 Pa
| Air Terminal | 250.0 CMH | - | - | - | - | - | - | 0.000 Pa
13 | Duct | 200.0 CMH | 160 mmø | 2.8 m/s | - | 498 | - | 0.73 Pa/m | 0.364 Pa | 208.521 Pa
| Fittings | 200.0 CMH | - | 2.8 m/s | 4.591 Pa | - | 45.3417 | - | 208.157 Pa
| Air Terminal | 200.0 CMH | - | - | - | - | - | - | 0.000 Pa
14 | Duct | 1150.0 CMH | 280 mmø | 5.2 m/s | - | 9949 | - | 1.14 Pa/m | 11.338 Pa | 33.764 Pa
| Fittings | 1150.0 CMH | - | 5.2 m/s | 16.184 Pa | - | 1.3857 | - | 22.426 Pa
15 | Duct | 2300.0 CMH | 400 mmx400 mm | 4.0 m/s | - | 2592 | - | 0.45 Pa/m | 1.174 Pa | 2.836 Pa
| Fittings | 2300.0 CMH | - | 4.0 m/s | 9.588 Pa | - | 0.17341 | - | 1.663 Pa
16 | Duct | 2300.0 CMH | 450 mmx450 mm | 3.2 m/s | - | 1172 | - | 0.26 Pa/m | 0.299 Pa | 0.655 Pa
| Fittings | 2300.0 CMH | - | 3.2 m/s | 5.985 Pa | - | 0.059412 | - | 0.356 Pa
17 | Duct | 2550.0 CMH | 450 mmx450 mm | 3.5 m/s | - | 1001 | - | 0.31 Pa/m | 0.308 Pa | 23.563 Pa
| Fittings | 2550.0 CMH | - | 3.5 m/s | 7.357 Pa | - | 3.1608 | - | 23.255 Pa
18 | Duct | 7300.0 CMH | 700 mmx700 mm | 4.1 m/s | - | 7935 | - | 0.25 Pa/m | 1.946 Pa | 13.813 Pa
| Fittings | 7300.0 CMH | - | 4.1 m/s | 10.298 Pa | - | 1.1524 | - | 11.867 Pa
19 | Duct | 7300.0 CMH | 1000 mmx500 mm | 4.1 m/s | - | 10425 | - | 0.25 Pa/m | 2.613 Pa | 49.195 Pa
| Fittings | 7300.0 CMH | - | 4.1 m/s | 9.890 Pa | - | 4.7101 | - | 46.583 Pa
20 | Duct | 7300.0 CMH | 1000 mmx500 mm | 4.1 m/s | - | 5622 | - | 0.25 Pa/m | 1.409 Pa | 2.136 Pa
| Fittings | 7300.0 CMH | - | 4.1 m/s | 9.890 Pa | - | 0.073512 | - | 0.727 Pa
21 | Duct | 7300.0 CMH | 1000 mmx1000 mm | 2.0 m/s | - | 1288 | - | 0.04 Pa/m | 0.055 Pa | 1.560 Pa
| Fittings | 7300.0 CMH | - | 2.0 m/s | 2.473 Pa | - | 0.60841 | - | 1.504 Pa
22 | Duct | 100.0 CMH | 160 mmø | 1.4 m/s | - | 2548 | - | 0.21 Pa/m | 0.540 Pa | 157.542 Pa
| Fittings | 100.0 CMH | - | 1.4 m/s | 1.148 Pa | - | 136.7954 | - | 157.002 Pa
| Air Terminal | 100.0 CMH | - | - | - | - | - | - | 0.000 Pa
23 | Duct | 400.0 CMH | 200 mmx200 mm | 2.8 m/s | - | 3403 | - | 0.56 Pa/m | 1.902 Pa | 2.459 Pa
| Fittings | 400.0 CMH | - | 2.8 m/s | 4.640 Pa | - | 0.12 | - | 0.557 Pa
24 | Duct | 500.0 CMH | 200 mmx200 mm | 3.5 m/s | - | 1415 | - | 0.84 Pa/m | 1.183 Pa | 1.183 Pa
| Fittings | 500.0 CMH | - | 3.5 m/s | 7.250 Pa | - | 0 | - | 0.000 Pa
25 | Duct | 500.0 CMH | 200 mmx200 mm | 3.5 m/s | - | 592 | - | 0.84 Pa/m | 0.495 Pa | 9.189 Pa
| Fittings | 500.0 CMH | - | 3.5 m/s | 7.250 Pa | - | 1.1993 | - | 8.695 Pa
26 | Fittings | 500.0 CMH | - | 0.0 m/s | 2.969 Pa | - | 10.5552 | - | 31.343 Pa | 31.343 Pa
27 | Duct | 500.0 CMH | 200 mmx200 mm | 3.5 m/s | - | 1016 | - | 0.84 Pa/m | 0.849 Pa | 21.916 Pa
| Fittings | 500.0 CMH | - | 3.5 m/s | 7.250 Pa | - | 2.9059 | - | 21.067 Pa
28 | Duct | 950.0 CMH | 300 mmx200 mm | 4.4 m/s | - | 161 | - | 1.02 Pa/m | 0.165 Pa | 0.165 Pa
| Fittings | 950.0 CMH | - | 4.4 m/s | 11.632 Pa | - | 0 | - | 0.000 Pa
29 | Duct | 950.0 CMH | 300 mmx200 mm | 4.4 m/s | - | 134 | - | 1.02 Pa/m | 0.137 Pa | 0.137 Pa
| Fittings | 950.0 CMH | - | 4.4 m/s | 11.632 Pa | - | 0 | - | 0.000 Pa
30 | Duct | 950.0 CMH | 300 mmx200 mm | 4.4 m/s | - | 464 | - | 1.02 Pa/m | 0.474 Pa | 0.474 Pa
| Fittings | 950.0 CMH | - | 4.4 m/s | 11.632 Pa | - | 0 | - | 0.000 Pa
31 | Duct | 950.0 CMH | 300 mmx200 mm | 4.4 m/s | - | 8903 | - | 1.02 Pa/m | 9.102 Pa | 12.120 Pa
| Fittings | 950.0 CMH | - | 4.4 m/s | 11.632 Pa | - | 0.25949 | - | 3.018 Pa
32 | Duct | 950.0 CMH | 350 mmx200 mm | 3.8 m/s | - | 2402 | - | 0.72 Pa/m | 1.724 Pa | 1.724 Pa
| Fittings | 950.0 CMH | - | 3.8 m/s | 8.546 Pa | - | 0 | - | 0.000 Pa
33 | Fittings | 950.0 CMH | - | 0.0 m/s | 11.632 Pa | - | 1.19 | - | 13.842 Pa | 13.842 Pa
34 | Duct | 950.0 CMH | 300 mmx200 mm | 4.4 m/s | - | 3466 | - | 1.02 Pa/m | 3.543 Pa | 18.199 Pa
| Fittings | 950.0 CMH | - | 4.4 m/s | 11.632 Pa | - | 1.26 | - | 14.656 Pa
35 | Duct | 950.0 CMH | 400 mmx300 mm | 2.2 m/s | - | 3169 | - | 0.19 Pa/m | 0.594 Pa | 7.346 Pa
| Fittings | 950.0 CMH | - | 2.2 m/s | 2.908 Pa | - | 2.3221 | - | 6.752 Pa
36 | Duct | 950.0 CMH | 350 mmx350 mm | 2.2 m/s | - | 3489 | - | 0.18 Pa/m | 0.614 Pa | 3.976 Pa
| Fittings | 950.0 CMH | - | 2.2 m/s | 2.790 Pa | - | 1.205 | - | 3.362 Pa
37 | Duct | 950.0 CMH | 500 mmx500 mm | 1.1 m/s | - | 1881 | - | 0.03 Pa/m | 0.060 Pa | 3.873 Pa
| Fittings | 950.0 CMH | - | 1.1 m/s | 0.670 Pa | - | 5.6912 | - | 3.813 Pa
38 | Duct | 100.0 CMH | 160 mmø | 1.4 m/s | - | 1897 | - | 0.21 Pa/m | 0.402 Pa | 189.181 Pa
| Fittings | 100.0 CMH | - | 1.4 m/s | 1.148 Pa | - | 164.4826 | - | 188.779 Pa
| Air Terminal | 100.0 CMH | - | - | - | - | - | - | 0.000 Pa
39 | Duct | 500.0 CMH | 200 mmx200 mm | 3.5 m/s | - | 3008 | - | 0.84 Pa/m | 2.515 Pa | 10.852 Pa
| Fittings | 500.0 CMH | - | 3.5 m/s | 7.250 Pa | - | 1.15 | - | 8.337 Pa
40 | Fittings | 500.0 CMH | - | 0.0 m/s | 2.969 Pa | - | 10.103 | - | 30.000 Pa | 30.000 Pa
41 | Fittings | 500.0 CMH | - | 0.0 m/s | 7.250 Pa | - | 0 | - | 0.000 Pa | 0.000 Pa
42 | Duct | 500.0 CMH | 200 mmx200 mm | 3.5 m/s | - | 563 | - | 0.84 Pa/m | 0.471 Pa | 55.264 Pa
| Fittings | 500.0 CMH | - | 3.5 m/s | 7.250 Pa | - | 7.5582 | - | 54.794 Pa
43 | Duct | 1299.8 CMH | 300 mmx300 mm | 4.0 m/s | - | 454 | - | 0.65 Pa/m | 0.297 Pa | 0.898 Pa
| Fittings | 1299.8 CMH | - | 4.0 m/s | 9.677 Pa | - | 0.062077 | - | 0.601 Pa
44 | Duct | 1449.8 CMH | 300 mmx300 mm | 4.5 m/s | - | 15402 | - | 0.80 Pa/m | 12.293 Pa | 51.930 Pa
| Fittings | 1449.8 CMH | - | 4.5 m/s | 12.040 Pa | - | 3.2921 | - | 39.636 Pa
45 | Duct | 1449.8 CMH | 400 mmx400 mm | 2.5 m/s | - | 566 | - | 0.20 Pa/m | 0.111 Pa | 0.643 Pa
| Fittings | 1449.8 CMH | - | 2.5 m/s | 3.810 Pa | - | 0.13949 | - | 0.531 Pa
46 | Duct | 1849.8 CMH | 400 mmx400 mm | 3.2 m/s | - | 1972 | - | 0.31 Pa/m | 0.602 Pa | 1.045 Pa
| Fittings | 1849.8 CMH | - | 3.2 m/s | 6.202 Pa | - | 0.071435 | - | 0.443 Pa
47 | Duct | 2099.8 CMH | 400 mmx400 mm | 3.6 m/s | - | 6306 | - | 0.38 Pa/m | 2.421 Pa | 17.537 Pa
| Fittings | 2099.8 CMH | - | 3.6 m/s | 7.991 Pa | - | 1.8916 | - | 15.116 Pa
48 | Duct | 150.0 CMH | 160 mmø | 2.1 m/s | - | 1363 | - | 0.44 Pa/m | 0.595 Pa | 195.414 Pa
| Fittings | 150.0 CMH | - | 2.1 m/s | 2.582 Pa | - | 75.4424 | - | 194.819 Pa
| Air Terminal | 150.0 CMH | - | - | - | - | - | - | 0.000 Pa
49 | Duct | 100.0 CMH | 160 mmø | 1.4 m/s | - | 385 | - | 0.21 Pa/m | 0.082 Pa | 193.725 Pa
| Fittings | 100.0 CMH | - | 1.4 m/s | 1.148 Pa | - | 168.721 | - | 193.643 Pa
| Air Terminal | 100.0 CMH | - | - | - | - | - | - | 0.000 Pa
50 | Duct | 600.0 CMH | 250 mmø | 3.4 m/s | - | 3190 | - | 0.61 Pa/m | 1.938 Pa | 50.458 Pa
| Fittings | 600.0 CMH | - | 3.4 m/s | 6.932 Pa | - | 6.9995 | - | 48.520 Pa
51 | Duct | 750.0 CMH | 250 mmø | 4.2 m/s | - | 3190 | - | 0.91 Pa/m | 2.904 Pa | 66.636 Pa
| Fittings | 750.0 CMH | - | 4.2 m/s | 10.831 Pa | - | 5.8841 | - | 63.732 Pa
52 | Fittings | 850.0 CMH | - | 0.0 m/s | 13.912 Pa | - | 0 | - | 0.000 Pa | 0.000 Pa
53 | Duct | 850.0 CMH | 300 mmx300 mm | 2.6 m/s | - | 2820 | - | 0.30 Pa/m | 0.857 Pa | 1.229 Pa
| Fittings | 850.0 CMH | - | 2.6 m/s | 4.139 Pa | - | 0.09 | - | 0.372 Pa
54 | Duct | 1000.0 CMH | 300 mmx300 mm | 3.1 m/s | - | 671 | - | 0.41 Pa/m | 0.273 Pa | 0.721 Pa
| Fittings | 1000.0 CMH | - | 3.1 m/s | 5.728 Pa | - | 0.078261 | - | 0.448 Pa
55 | Duct | 1150.0 CMH | 300 mmx300 mm | 3.5 m/s | - | 2108 | - | 0.52 Pa/m | 1.105 Pa | 3.360 Pa
| Fittings | 1150.0 CMH | - | 3.5 m/s | 7.575 Pa | - | 0.29767 | - | 2.255 Pa
56 | Fittings | 1150.0 CMH | - | 0.0 m/s | 12.523 Pa | - | 1.2014 | - | 15.045 Pa | 15.045 Pa
57 | Duct | 1150.0 CMH | 350 mmx200 mm | 4.6 m/s | - | 500 | - | 1.02 Pa/m | 0.508 Pa | 0.508 Pa
| Fittings | 1150.0 CMH | - | 4.6 m/s | 12.523 Pa | - | 0 | - | 0.000 Pa
58 | Duct | 1150.0 CMH | 350 mmx200 mm | 4.6 m/s | - | 2200 | - | 1.02 Pa/m | 2.235 Pa | 2.900 Pa
| Fittings | 1150.0 CMH | - | 4.6 m/s | 12.523 Pa | - | 0.053126 | - | 0.665 Pa
59 | Duct | 1150.0 CMH | 400 mmx400 mm | 2.0 m/s | - | 520 | - | 0.13 Pa/m | 0.068 Pa | 8.369 Pa
| Fittings | 1150.0 CMH | - | 2.0 m/s | 2.397 Pa | - | 3.4634 | - | 8.301 Pa
60 | Duct | 150.0 CMH | 160 mmø | 2.1 m/s | - | 611 | - | 0.44 Pa/m | 0.267 Pa | 13.229 Pa
| Fittings | 150.0 CMH | - | 2.1 m/s | 2.582 Pa | - | 5.0196 | - | 12.962 Pa
| Air Terminal | 150.0 CMH | - | - | - | - | - | - | 0.000 Pa
61 | Duct | 300.0 CMH | 160 mmø | 4.1 m/s | - | 14810 | - | 1.52 Pa/m | 22.560 Pa | 206.560 Pa
| Fittings | 300.0 CMH | - | 4.1 m/s | 10.329 Pa | - | 17.8132 | - | 184.000 Pa
62 | Fittings | 300.0 CMH | - | 0.0 m/s | 2.610 Pa | - | 0.033333 | - | 0.087 Pa | 0.087 Pa
63 | Duct | 300.0 CMH | 300 mmx200 mm | 1.4 m/s | - | 439 | - | 0.13 Pa/m | 0.057 Pa | 0.428 Pa
| Fittings | 300.0 CMH | - | 1.4 m/s | 1.160 Pa | - | 0.32 | - | 0.371 Pa
64 | Duct | 450.0 CMH | 300 mmx200 mm | 2.1 m/s | - | 0 | - | 0.27 Pa/m | 0.000 Pa | 0.915 Pa
| Fittings | 450.0 CMH | - | 2.1 m/s | 2.610 Pa | - | 0.35053 | - | 0.915 Pa
65 | Duct | 100.0 CMH | 160 mmø | 1.4 m/s | - | 1756 | - | 0.21 Pa/m | 0.372 Pa | 187.374 Pa
| Fittings | 100.0 CMH | - | 1.4 m/s | 1.148 Pa | - | 162.9344 | - | 187.002 Pa
| Air Terminal | 100.0 CMH | - | - | - | - | - | - | 0.000 Pa
66 | Duct | 400.0 CMH | 200 mmx200 mm | 2.8 m/s | - | 3403 | - | 0.56 Pa/m | 1.902 Pa | 2.459 Pa
| Fittings | 400.0 CMH | - | 2.8 m/s | 4.640 Pa | - | 0.12 | - | 0.557 Pa
67 | Duct | 100.0 CMH | 160 mmø | 1.4 m/s | - | 1756 | - | 0.21 Pa/m | 0.372 Pa | 183.797 Pa
| Fittings | 100.0 CMH | - | 1.4 m/s | 1.148 Pa | - | 159.8179 | - | 183.425 Pa
| Air Terminal | 100.0 CMH | - | - | - | - | - | - | 0.000 Pa
68 | Duct | 200.0 CMH | 200 mmx200 mm | 1.4 m/s | - | 3450 | - | 0.16 Pa/m | 0.559 Pa | 0.930 Pa
| Fittings | 200.0 CMH | - | 1.4 m/s | 1.160 Pa | - | 0.32 | - | 0.371 Pa
69 | Duct | 300.0 CMH | 200 mmx200 mm | 2.1 m/s | - | 3450 | - | 0.33 Pa/m | 1.151 Pa | 1.621 Pa
| Fittings | 300.0 CMH | - | 2.1 m/s | 2.610 Pa | - | 0.18 | - | 0.470 Pa
70 | Duct | 150.0 CMH | 160 mmø | 2.1 m/s | - | 3326 | - | 0.44 Pa/m | 1.453 Pa | 203.560 Pa
| Fittings | 150.0 CMH | - | 2.1 m/s | 2.582 Pa | - | 78.2648 | - | 202.107 Pa
| Air Terminal | 150.0 CMH | - | - | - | - | - | - | 0.000 Pa
71 | Duct | 950.0 CMH | 280 mmø | 4.3 m/s | - | 5660 | - | 0.80 Pa/m | 4.552 Pa | 72.511 Pa
| Fittings | 950.0 CMH | - | 4.3 m/s | 11.044 Pa | - | 6.1534 | - | 67.958 Pa
72 | Duct | 100.0 CMH | 160 mmø | 1.4 m/s | - | 1852 | - | 0.21 Pa/m | 0.393 Pa | 182.793 Pa
| Fittings | 100.0 CMH | - | 1.4 m/s | 1.148 Pa | - | 158.9248 | - | 182.400 Pa
| Air Terminal | 100.0 CMH | - | - | - | - | - | - | 0.000 Pa
73 | Duct | 100.0 CMH | 200 mmx200 mm | 0.7 m/s | - | 385 | - | 0.05 Pa/m | 0.018 Pa | 0.305 Pa
| Fittings | 100.0 CMH | - | 0.7 m/s | 0.290 Pa | - | 0.99 | - | 0.287 Pa
74 | Duct | 250.0 CMH | 250 mmø | 1.4 m/s | - | 3520 | - | 0.13 Pa/m | 0.446 Pa | 41.946 Pa
| Fittings | 250.0 CMH | - | 1.4 m/s | 1.203 Pa | - | 34.4842 | - | 41.500 Pa
| Air Terminal | 250.0 CMH | - | - | - | - | - | - | 0.000 Pa
75 | Duct | 150.0 CMH | 160 mmø | 2.1 m/s | - | 6852 | - | 0.44 Pa/m | 2.993 Pa | 196.983 Pa
| Fittings | 150.0 CMH | - | 2.1 m/s | 2.582 Pa | - | 75.1214 | - | 193.990 Pa
| Air Terminal | 150.0 CMH | - | - | - | - | - | - | 0.000 Pa
76 | Duct | 250.0 CMH | 250 mmø | 1.4 m/s | - | 3550 | - | 0.13 Pa/m | 0.449 Pa | 40.993 Pa
| Fittings | 250.0 CMH | - | 1.4 m/s | 1.203 Pa | - | 33.6889 | - | 40.543 Pa
| Air Terminal | 250.0 CMH | - | - | - | - | - | - | 0.000 Pa
77 | Duct | 200.0 CMH | 160 mmø | 2.8 m/s | - | 661 | - | 0.73 Pa/m | 0.483 Pa | 18.626 Pa
| Fittings | 200.0 CMH | - | 2.8 m/s | 4.591 Pa | - | 3.952 | - | 18.143 Pa
| Air Terminal | 200.0 CMH | - | - | - | - | - | - | 0.000 Pa
78 | Duct | 400.0 CMH | 180 mmø | 4.4 m/s | - | 13022 | - | 1.45 Pa/m | 18.823 Pa | 53.079 Pa
| Fittings | 400.0 CMH | - | 4.4 m/s | 11.464 Pa | - | 2.9881 | - | 34.256 Pa
79 | Duct | 400.0 CMH | 250 mmø | 2.3 m/s | - | 58 | - | 0.29 Pa/m | 0.017 Pa | 13.573 Pa
| Fittings | 400.0 CMH | - | 2.3 m/s | 3.081 Pa | - | 4.4 | - | 13.556 Pa
80 | Duct | 800.0 CMH | 250 mmø | 4.5 m/s | - | 8106 | - | 1.02 Pa/m | 8.300 Pa | 31.950 Pa
| Fittings | 800.0 CMH | - | 4.5 m/s | 12.323 Pa | - | 1.9191 | - | 23.650 Pa
81 | Duct | 800.0 CMH | 280 mmø | 3.6 m/s | - | 135 | - | 0.59 Pa/m | 0.079 Pa | 52.073 Pa
| Fittings | 800.0 CMH | - | 3.6 m/s | 7.832 Pa | - | 6.6387 | - | 51.993 Pa
82 | Duct | 266.6 CMH | 250 mmø | 1.5 m/s | - | 463 | - | 0.14 Pa/m | 0.066 Pa | 12.368 Pa
| Fittings | 266.6 CMH | - | 1.5 m/s | 1.369 Pa | - | 8.9891 | - | 12.302 Pa
| Air Terminal | 266.6 CMH | - | - | - | - | - | - | 0.000 Pa
83 | Duct | 799.8 CMH | 250 mmø | 4.5 m/s | - | 3010 | - | 1.02 Pa/m | 3.081 Pa | 13.655 Pa
| Fittings | 799.8 CMH | - | 4.5 m/s | 12.317 Pa | - | 0.85847 | - | 10.574 Pa
84 | Duct | 799.8 CMH | 200 mmø | 7.1 m/s | - | 194 | - | 3.07 Pa/m | 0.595 Pa | 182.337 Pa
| Fittings | 799.8 CMH | - | 7.1 m/s | 30.072 Pa | - | 6.0436 | - | 181.742 Pa
85 | Fittings | 799.8 CMH | - | 0.0 m/s | 3.664 Pa | - | 0 | - | 0.000 Pa | 0.000 Pa
86 | Duct | 799.8 CMH | 300 mmx300 mm | 2.5 m/s | - | 264 | - | 0.27 Pa/m | 0.072 Pa | 5.910 Pa
| Fittings | 799.8 CMH | - | 2.5 m/s | 3.664 Pa | - | 1.5932 | - | 5.838 Pa
87 | Duct | 100.0 CMH | 160 mmø | 1.4 m/s | - | 1888 | - | 0.21 Pa/m | 0.400 Pa | 189.179 Pa
| Fittings | 100.0 CMH | - | 1.4 m/s | 1.148 Pa | - | 164.4826 | - | 188.779 Pa
| Air Terminal | 100.0 CMH | - | - | - | - | - | - | 0.000 Pa
88 | Duct | 150.0 CMH | 160 mmø | 2.1 m/s | - | 1273 | - | 0.44 Pa/m | 0.556 Pa | 191.391 Pa
| Fittings | 150.0 CMH | - | 2.1 m/s | 2.582 Pa | - | 73.8995 | - | 190.835 Pa
| Air Terminal | 150.0 CMH | - | - | - | - | - | - | 0.000 Pa
89 | Duct | 949.8 CMH | 300 mmx300 mm | 2.9 m/s | - | 1351 | - | 0.37 Pa/m | 0.501 Pa | 2.298 Pa
| Fittings | 949.8 CMH | - | 2.9 m/s | 5.167 Pa | - | 0.3477 | - | 1.797 Pa
90 | Duct | 1449.8 CMH | 300 mmx300 mm | 4.5 m/s | - | 9746 | - | 0.80 Pa/m | 7.779 Pa | 7.779 Pa
| Fittings | 1449.8 CMH | - | 4.5 m/s | 12.040 Pa | - | 0 | - | 0.000 Pa
91 | Duct | 1449.8 CMH | 300 mmx300 mm | 4.5 m/s | - | 4147 | - | 0.80 Pa/m | 3.310 Pa | 42.947 Pa
| Fittings | 1449.8 CMH | - | 4.5 m/s | 12.040 Pa | - | 3.2921 | - | 39.636 Pa
92 | Duct | 1449.8 CMH | 400 mmx400 mm | 2.5 m/s | - | 276 | - | 0.20 Pa/m | 0.054 Pa | 1.056 Pa
| Fittings | 1449.8 CMH | - | 2.5 m/s | 3.810 Pa | - | 0.26293 | - | 1.002 Pa
93 | Duct | 100.0 CMH | 160 mmø | 1.4 m/s | - | 1747 | - | 0.21 Pa/m | 0.370 Pa | 181.970 Pa
| Fittings | 100.0 CMH | - | 1.4 m/s | 1.148 Pa | - | 158.2278 | - | 181.600 Pa
| Air Terminal | 100.0 CMH | - | - | - | - | - | - | 0.000 Pa
94 | Duct | 200.0 CMH | 200 mmx200 mm | 1.4 m/s | - | 3450 | - | 0.16 Pa/m | 0.559 Pa | 0.930 Pa
| Fittings | 200.0 CMH | - | 1.4 m/s | 1.160 Pa | - | 0.32 | - | 0.371 Pa
95 | Duct | 300.0 CMH | 200 mmx200 mm | 2.1 m/s | - | 3450 | - | 0.33 Pa/m | 1.151 Pa | 1.621 Pa
| Fittings | 300.0 CMH | - | 2.1 m/s | 2.610 Pa | - | 0.18 | - | 0.470 Pa
96 | Duct | 100.0 CMH | 160 mmø | 1.4 m/s | - | 1840 | - | 0.21 Pa/m | 0.390 Pa | 184.494 Pa
| Fittings | 100.0 CMH | - | 1.4 m/s | 1.148 Pa | - | 160.4097 | - | 184.104 Pa
| Air Terminal | 100.0 CMH | - | - | - | - | - | - | 0.000 Pa
97 | Duct | 150.0 CMH | 160 mmø | 2.1 m/s | - | 3596 | - | 0.44 Pa/m | 1.571 Pa | 36.333 Pa
| Fittings | 150.0 CMH | - | 2.1 m/s | 2.582 Pa | - | 13.4615 | - | 34.762 Pa
| Air Terminal | 150.0 CMH | - | - | - | - | - | - | 0.000 Pa
98 | Duct | 150.0 CMH | 160 mmø | 2.1 m/s | - | 273 | - | 0.44 Pa/m | 0.119 Pa | 185.992 Pa
| Fittings | 150.0 CMH | - | 2.1 m/s | 2.582 Pa | - | 71.9781 | - | 185.873 Pa
| Air Terminal | 150.0 CMH | - | - | - | - | - | - | 0.000 Pa
99 | Duct | 250.0 CMH | 250 mmø | 1.4 m/s | - | 1797 | - | 0.13 Pa/m | 0.227 Pa | 3.718 Pa
| Fittings | 250.0 CMH | - | 1.4 m/s | 1.203 Pa | - | 2.9 | - | 3.490 Pa
| Air Terminal | 250.0 CMH | - | - | - | - | - | - | 0.000 Pa
100 | Duct | 500.0 CMH | 250 mmø | 2.8 m/s | - | 5366 | - | 0.44 Pa/m | 2.346 Pa | 74.364 Pa
| Fittings | 500.0 CMH | - | 2.8 m/s | 4.814 Pa | - | 14.9606 | - | 72.018 Pa
101 | Duct | 266.6 CMH | 250 mmø | 1.5 m/s | - | 538 | - | 0.14 Pa/m | 0.076 Pa | 13.046 Pa
| Fittings | 266.6 CMH | - | 1.5 m/s | 1.369 Pa | - | 9.4767 | - | 12.970 Pa
| Air Terminal | 266.6 CMH | - | - | - | - | - | - | 0.000 Pa
102 | Duct | 799.8 CMH | 250 mmø | 4.5 m/s | - | 3725 | - | 1.02 Pa/m | 3.812 Pa | 12.884 Pa
| Fittings | 799.8 CMH | - | 4.5 m/s | 12.317 Pa | - | 0.73653 | - | 9.072 Pa
103 | Fittings | 799.8 CMH | - | 0.0 m/s | 30.072 Pa | - | 6.0217 | - | 181.083 Pa | 181.083 Pa
104 | Duct | 799.8 CMH | 250 mmø | 4.5 m/s | - | 560 | - | 1.02 Pa/m | 0.573 Pa | 3.677 Pa
| Fittings | 799.8 CMH | - | 4.5 m/s | 12.317 Pa | - | 0.25198 | - | 3.104 Pa
105 | Duct | 799.8 CMH | 300 mmx300 mm | 0.0 m/s | - | 715 | - | 0.00 Pa/m | 0.000 Pa | 0.000 Pa
| Fittings | 799.8 CMH | - | 0.0 m/s | 0.000 Pa | - | 0 | - | 0.000 Pa
106 | Duct | 100.0 CMH | 160 mmø | 1.4 m/s | - | 1836 | - | 0.21 Pa/m | 0.389 Pa | 182.789 Pa
| Fittings | 100.0 CMH | - | 1.4 m/s | 1.148 Pa | - | 158.9248 | - | 182.400 Pa
| Air Terminal | 100.0 CMH | - | - | - | - | - | - | 0.000 Pa
107 | Duct | 100.0 CMH | 200 mmx200 mm | 0.7 m/s | - | 385 | - | 0.05 Pa/m | 0.018 Pa | 0.305 Pa
| Fittings | 100.0 CMH | - | 0.7 m/s | 0.290 Pa | - | 0.99 | - | 0.287 Pa
108 | Duct | 200.0 CMH | 200 mmx200 mm | 1.4 m/s | - | 3450 | - | 0.16 Pa/m | 0.559 Pa | 0.930 Pa
| Fittings | 200.0 CMH | - | 1.4 m/s | 1.160 Pa | - | 0.32 | - | 0.371 Pa
109 | Duct | 300.0 CMH | 200 mmx200 mm | 2.1 m/s | - | 3450 | - | 0.33 Pa/m | 1.151 Pa | 1.621 Pa
| Fittings | 300.0 CMH | - | 2.1 m/s | 2.610 Pa | - | 0.18 | - | 0.470 Pa
110 | Duct | 400.0 CMH | 200 mmx200 mm | 2.8 m/s | - | 3403 | - | 0.56 Pa/m | 1.902 Pa | 1.902 Pa
| Fittings | 400.0 CMH | - | 2.8 m/s | 4.640 Pa | - | 0 | - | 0.000 Pa
111 | Duct | 500.0 CMH | 200 mmx200 mm | 3.5 m/s | - | 602 | - | 0.84 Pa/m | 0.503 Pa | 0.503 Pa
| Fittings | 500.0 CMH | - | 3.5 m/s | 7.250 Pa | - | 0 | - | 0.000 Pa
112 | Duct | 500.0 CMH | 200 mmx200 mm | 3.5 m/s | - | 1948 | - | 0.84 Pa/m | 1.629 Pa | 9.966 Pa
| Fittings | 500.0 CMH | - | 3.5 m/s | 7.250 Pa | - | 1.15 | - | 8.337 Pa
113 | Fittings | 500.0 CMH | - | 0.0 m/s | 2.969 Pa | - | 10.103 | - | 30.000 Pa | 30.000 Pa
114 | Duct | 500.0 CMH | 200 mmx200 mm | 3.5 m/s | - | 1804 | - | 0.84 Pa/m | 1.508 Pa | 59.597 Pa
| Fittings | 500.0 CMH | - | 3.5 m/s | 7.250 Pa | - | 8.0127 | - | 58.088 Pa
115 | Duct | 250.0 CMH | 250 mmø | 1.4 m/s | - | 8773 | - | 0.13 Pa/m | 1.110 Pa | 41.007 Pa
| Fittings | 250.0 CMH | - | 1.4 m/s | 1.203 Pa | - | 33.1515 | - | 39.897 Pa
| Air Terminal | 250.0 CMH | - | - | - | - | - | - | 0.000 Pa
116 | Duct | 400.0 CMH | 250 mmø | 2.3 m/s | - | 6301 | - | 0.29 Pa/m | 1.845 Pa | 32.417 Pa
| Fittings | 400.0 CMH | - | 2.3 m/s | 3.081 Pa | - | 9.9231 | - | 30.572 Pa
117 | Duct | 200.0 CMH | 160 mmø | 2.8 m/s | - | 4763 | - | 0.73 Pa/m | 3.486 Pa | 5.982 Pa
| Fittings | 200.0 CMH | - | 2.8 m/s | 4.591 Pa | - | 0.54377 | - | 2.496 Pa
| Air Terminal | 200.0 CMH | - | - | - | - | - | - | 0.000 Pa
118 | Fittings | 200.0 CMH | - | 0.0 m/s | 2.866 Pa | - | 4.4 | - | 12.611 Pa | 12.611 Pa
119 | Duct | 150.0 CMH | 160 mmø | 2.1 m/s | - | 7197 | - | 0.44 Pa/m | 3.143 Pa | 194.411 Pa
| Fittings | 150.0 CMH | - | 2.1 m/s | 2.582 Pa | - | 74.0673 | - | 191.268 Pa
| Air Terminal | 150.0 CMH | - | - | - | - | - | - | 0.000 Pa
120 | Duct | 150.0 CMH | 160 mmø | 2.1 m/s | - | 726 | - | 0.44 Pa/m | 0.317 Pa | 193.567 Pa
| Fittings | 150.0 CMH | - | 2.1 m/s | 2.582 Pa | - | 74.8347 | - | 193.250 Pa
| Air Terminal | 150.0 CMH | - | - | - | - | - | - | 0.000 Pa
121 | Duct | 150.0 CMH | 160 mmø | 2.1 m/s | - | 554 | - | 0.44 Pa/m | 0.242 Pa | 192.573 Pa
| Fittings | 150.0 CMH | - | 2.1 m/s | 2.582 Pa | - | 74.479 | - | 192.331 Pa
| Air Terminal | 150.0 CMH | - | - | - | - | - | - | 0.000 Pa
122 | Duct | 266.6 CMH | 250 mmø | 1.5 m/s | - | 6318 | - | 0.14 Pa/m | 0.896 Pa | 30.318 Pa
| Fittings | 266.6 CMH | - | 1.5 m/s | 1.369 Pa | - | 21.4979 | - | 29.422 Pa
| Air Terminal | 266.6 CMH | - | - | - | - | - | - | 0.000 Pa
123 | Duct | 533.2 CMH | 250 mmø | 3.0 m/s | - | 5926 | - | 0.49 Pa/m | 2.909 Pa | 3.657 Pa
| Fittings | 533.2 CMH | - | 3.0 m/s | 5.474 Pa | - | 0.13667 | - | 0.748 Pa
124 | Duct | 100.0 CMH | 160 mmø | 1.4 m/s | - | 483 | - | 0.21 Pa/m | 0.102 Pa | 200.665 Pa
| Fittings | 100.0 CMH | - | 1.4 m/s | 1.148 Pa | - | 174.7495 | - | 200.562 Pa
| Air Terminal | 100.0 CMH | - | - | - | - | - | - | 0.000 Pa
125 | Duct | 100.0 CMH | 160 mmø | 1.4 m/s | - | 1756 | - | 0.21 Pa/m | 0.372 Pa | 185.187 Pa
| Fittings | 100.0 CMH | - | 1.4 m/s | 1.148 Pa | - | 161.0287 | - | 184.815 Pa
| Air Terminal | 100.0 CMH | - | - | - | - | - | - | 0.000 Pa
126 | Duct | 150.0 CMH | 160 mmø | 2.1 m/s | - | 575 | - | 0.44 Pa/m | 0.251 Pa | 196.362 Pa
| Fittings | 150.0 CMH | - | 2.1 m/s | 2.582 Pa | - | 75.9427 | - | 196.111 Pa
| Air Terminal | 150.0 CMH | - | - | - | - | - | - | 0.000 Pa
127 | Duct | 250.0 CMH | 250 mmø | 1.4 m/s | - | 1802 | - | 0.13 Pa/m | 0.228 Pa | 24.718 Pa
| Fittings | 250.0 CMH | - | 1.4 m/s | 1.203 Pa | - | 20.3496 | - | 24.490 Pa
| Air Terminal | 250.0 CMH | - | - | - | - | - | - | 0.000 Pa
128 | Duct | 266.6 CMH | - | 1.5 m/s | - | 535 | - | 0.14 Pa/m | 0.076 Pa | 6.098 Pa
| Fittings | 266.6 CMH | - | 1.5 m/s | 1.369 Pa | - | 4.4 | - | 6.022 Pa
| Air Terminal | 266.6 CMH | - | - | - | - | - | - | 0.000 Pa
129 | Duct | 533.2 CMH | 250 mmø | 3.0 m/s | - | 5911 | - | 0.49 Pa/m | 2.901 Pa | 45.635 Pa
| Fittings | 533.2 CMH | - | 3.0 m/s | 5.474 Pa | - | 7.8061 | - | 42.733 Pa
130 | Duct | 266.6 CMH | 250 mmø | 1.5 m/s | - | 5921 | - | 0.14 Pa/m | 0.840 Pa | 28.662 Pa
| Fittings | 266.6 CMH | - | 1.5 m/s | 1.369 Pa | - | 20.3288 | - | 27.822 Pa
| Air Terminal | 266.6 CMH | - | - | - | - | - | - | 0.000 Pa
131 | Duct | 400.0 CMH | 250 mmø | 2.3 m/s | - | 3551 | - | 0.29 Pa/m | 1.040 Pa | 51.735 Pa
| Fittings | 400.0 CMH | - | 2.3 m/s | 3.081 Pa | - | 16.4549 | - | 50.695 Pa
| Air Terminal | 400.0 CMH | - | - | - | - | - | - | 0.000 Pa
132 | Duct | 266.6 CMH | 250 mmø | 1.5 m/s | - | 447 | - | 0.14 Pa/m | 0.063 Pa | 7.685 Pa
| Fittings | 266.6 CMH | - | 1.5 m/s | 1.369 Pa | - | 5.5691 | - | 7.622 Pa
| Air Terminal | 266.6 CMH | - | - | - | - | - | - | 0.000 Pa
133 | Duct | 125.0 CMH | 160 mmø | 1.7 m/s | - | 252 | - | 0.32 Pa/m | 0.080 Pa | 8.770 Pa
| Fittings | 125.0 CMH | - | 1.7 m/s | 1.793 Pa | - | 4.8461 | - | 8.691 Pa
| Air Terminal | 125.0 CMH | - | - | - | - | - | - | 0.000 Pa
134 | Duct | 250.0 CMH | 160 mmø | 3.5 m/s | - | 4602 | - | 1.09 Pa/m | 5.037 Pa | 188.586 Pa
| Fittings | 250.0 CMH | - | 3.5 m/s | 7.173 Pa | - | 25.5882 | - | 183.550 Pa
135 | Fittings | 250.0 CMH | - | 0.0 m/s | 1.203 Pa | - | 3.9529 | - | 4.757 Pa | 4.757 Pa
136 | Duct | 350.0 CMH | 250 mmø | 2.0 m/s | - | 3191 | - | 0.23 Pa/m | 0.736 Pa | 31.053 Pa
| Fittings | 350.0 CMH | - | 2.0 m/s | 2.359 Pa | - | 12.8529 | - | 30.317 Pa
137 | Duct | 500.0 CMH | 250 mmø | 2.8 m/s | - | 3190 | - | 0.44 Pa/m | 1.395 Pa | 41.457 Pa
| Fittings | 500.0 CMH | - | 2.8 m/s | 4.814 Pa | - | 8.3224 | - | 40.063 Pa
138 | Duct | 600.0 CMH | 250 mmø | 3.4 m/s | - | 3190 | - | 0.61 Pa/m | 1.938 Pa | 71.458 Pa
| Fittings | 600.0 CMH | - | 3.4 m/s | 6.932 Pa | - | 10.0289 | - | 69.520 Pa
139 | Duct | 750.0 CMH | 250 mmø | 4.2 m/s | - | 209 | - | 0.91 Pa/m | 0.190 Pa | 0.410 Pa
| Fittings | 750.0 CMH | - | 4.2 m/s | 10.831 Pa | - | 0.020281 | - | 0.220 Pa
140 | Fittings | 750.0 CMH | - | 0.0 m/s | 6.883 Pa | - | 3.96 | - | 27.258 Pa | 27.258 Pa
141 | Duct | 900.0 CMH | 280 mmø | 4.1 m/s | - | 5360 | - | 0.73 Pa/m | 3.907 Pa | 27.870 Pa
| Fittings | 900.0 CMH | - | 4.1 m/s | 9.912 Pa | - | 2.4176 | - | 23.963 Pa
142 | Duct | 900.0 CMH | 400 mmx400 mm | 1.6 m/s | - | 340 | - | 0.08 Pa/m | 0.029 Pa | 2.583 Pa
| Fittings | 900.0 CMH | - | 1.6 m/s | 1.468 Pa | - | 1.74 | - | 2.554 Pa
143 | Duct | 2100.0 CMH | 400 mmx400 mm | 3.6 m/s | - | 3713 | - | 0.38 Pa/m | 1.426 Pa | 19.809 Pa
| Fittings | 2100.0 CMH | - | 3.6 m/s | 7.993 Pa | - | 2.3 | - | 18.383 Pa
144 | Duct | 2100.0 CMH | 450 mmx450 mm | 2.9 m/s | - | 1172 | - | 0.22 Pa/m | 0.254 Pa | 0.572 Pa
| Fittings | 2100.0 CMH | - | 2.9 m/s | 4.990 Pa | - | 0.06383 | - | 0.318 Pa
145 | Duct | 2350.0 CMH | 450 mmx450 mm | 3.2 m/s | - | 1051 | - | 0.27 Pa/m | 0.279 Pa | 19.028 Pa
| Fittings | 2350.0 CMH | - | 3.2 m/s | 6.249 Pa | - | 3.0005 | - | 18.749 Pa
146 | Duct | 4750.0 CMH | 600 mmx600 mm | 3.7 m/s | - | 2929 | - | 0.24 Pa/m | 0.692 Pa | 0.992 Pa
| Fittings | 4750.0 CMH | - | 3.7 m/s | 8.077 Pa | - | 0.037143 | - | 0.300 Pa
147 | Duct | 4750.0 CMH | 700 mmx700 mm | 2.7 m/s | - | 855 | - | 0.11 Pa/m | 0.095 Pa | 1.658 Pa
| Fittings | 4750.0 CMH | - | 2.7 m/s | 4.360 Pa | - | 0.35836 | - | 1.562 Pa
148 | Duct | 175.0 CMH | 160 mmø | 2.4 m/s | - | 4971 | - | 0.58 Pa/m | 2.862 Pa | 20.727 Pa
| Fittings | 175.0 CMH | - | 2.4 m/s | 3.515 Pa | - | 5.0828 | - | 17.865 Pa
| Air Terminal | 175.0 CMH | - | - | - | - | - | - | 0.000 Pa
149 | Duct | 350.0 CMH | 160 mmø | 4.8 m/s | - | 7475 | - | 2.02 Pa/m | 15.078 Pa | 219.150 Pa
| Fittings | 350.0 CMH | - | 4.8 m/s | 14.059 Pa | - | 14.5149 | - | 204.072 Pa
150 | Fittings | 350.0 CMH | - | 0.0 m/s | 1.499 Pa | - | 7.7995 | - | 11.692 Pa | 11.692 Pa
151 | Duct | 950.0 CMH | 280 mmø | 4.3 m/s | - | 12810 | - | 0.80 Pa/m | 10.303 Pa | 103.070 Pa
| Fittings | 950.0 CMH | - | 4.3 m/s | 11.044 Pa | - | 8.3998 | - | 92.767 Pa
152 | Duct | 1075.0 CMH | 280 mmø | 4.8 m/s | - | 5807 | - | 1.01 Pa/m | 5.851 Pa | 64.786 Pa
| Fittings | 1075.0 CMH | - | 4.8 m/s | 14.142 Pa | - | 4.1675 | - | 58.935 Pa
153 | Duct | 1200.0 CMH | 280 mmø | 5.4 m/s | - | 9352 | - | 1.23 Pa/m | 11.521 Pa | 53.815 Pa
| Fittings | 1200.0 CMH | - | 5.4 m/s | 17.622 Pa | - | 2.4001 | - | 42.294 Pa
154 | Duct | 300.0 CMH | - | 2.7 m/s | - | 486 | - | 0.51 Pa/m | 0.250 Pa | 0.402 Pa
| Fittings | 300.0 CMH | - | 2.7 m/s | 4.231 Pa | - | 0.036 | - | 0.152 Pa
| Air Terminal | 300.0 CMH | - | - | - | - | - | - | 0.000 Pa
155 | Fittings | 300.0 CMH | - | 0.0 m/s | 1.733 Pa | - | 15.0178 | - | 26.026 Pa | 26.026 Pa
156 | Duct | 600.0 CMH | 250 mmø | 3.4 m/s | - | 1982 | - | 0.61 Pa/m | 1.204 Pa | 57.878 Pa
| Fittings | 600.0 CMH | - | 3.4 m/s | 6.932 Pa | - | 8.1757 | - | 56.674 Pa
157 | Duct | 125.0 CMH | 160 mmø | 1.7 m/s | - | 3103 | - | 0.32 Pa/m | 0.979 Pa | 10.469 Pa
| Fittings | 125.0 CMH | - | 1.7 m/s | 1.793 Pa | - | 5.2922 | - | 9.491 Pa
| Air Terminal | 125.0 CMH | - | - | - | - | - | - | 0.000 Pa
158 | Duct | 250.0 CMH | 160 mmø | 3.5 m/s | - | 542 | - | 1.09 Pa/m | 0.593 Pa | 231.708 Pa
| Fittings | 250.0 CMH | - | 3.5 m/s | 7.173 Pa | - | 32.2192 | - | 231.115 Pa
159 | Duct | 850.0 CMH | 280 mmø | 3.8 m/s | - | 3569 | - | 0.66 Pa/m | 2.346 Pa | 5.311 Pa
| Fittings | 850.0 CMH | - | 3.8 m/s | 8.841 Pa | - | 0.33544 | - | 2.966 Pa
160 | Duct | 850.0 CMH | 400 mmx300 mm | 2.0 m/s | - | 246 | - | 0.15 Pa/m | 0.038 Pa | 10.329 Pa
| Fittings | 850.0 CMH | - | 2.0 m/s | 2.328 Pa | - | 4.4208 | - | 10.291 Pa
161 | Duct | 2400.0 CMH | 400 mmx300 mm | 5.6 m/s | - | 3295 | - | 1.00 Pa/m | 3.305 Pa | 41.266 Pa
| Fittings | 2400.0 CMH | - | 5.6 m/s | 18.559 Pa | - | 2.0454 | - | 37.961 Pa
162 | Fittings | 2400.0 CMH | - | 0.0 m/s | 10.439 Pa | - | 0.19426 | - | 2.028 Pa | 2.028 Pa
163 | Duct | 2400.0 CMH | 400 mmx300 mm | 5.6 m/s | - | 100 | - | 1.00 Pa/m | 0.100 Pa | 0.564 Pa
| Fittings | 2400.0 CMH | - | 5.6 m/s | 18.559 Pa | - | 0.025 | - | 0.464 Pa
164 | Duct | 2400.0 CMH | 400 mmx400 mm | 4.2 m/s | - | 4424 | - | 0.49 Pa/m | 2.164 Pa | 26.717 Pa
| Fittings | 2400.0 CMH | - | 4.2 m/s | 10.439 Pa | - | 2.3519 | - | 24.553 Pa
165 | Duct | 2400.0 CMH | 600 mmx600 mm | 1.9 m/s | - | 871 | - | 0.07 Pa/m | 0.060 Pa | 2.046 Pa
| Fittings | 2400.0 CMH | - | 1.9 m/s | 2.062 Pa | - | 0.96316 | - | 1.986 Pa
166 | Duct | 150.0 CMH | 160 mmø | 2.1 m/s | - | 392 | - | 0.44 Pa/m | 0.171 Pa | 191.989 Pa
| Fittings | 150.0 CMH | - | 2.1 m/s | 2.582 Pa | - | 74.2801 | - | 191.817 Pa
| Air Terminal | 150.0 CMH | - | - | - | - | - | - | 0.000 Pa
167 | Duct | 100.0 CMH | 160 mmø | 1.4 m/s | - | 493 | - | 0.21 Pa/m | 0.104 Pa | 193.748 Pa
| Fittings | 100.0 CMH | - | 1.4 m/s | 1.148 Pa | - | 168.721 | - | 193.643 Pa
| Air Terminal | 100.0 CMH | - | - | - | - | - | - | 0.000 Pa
168 | Duct | 150.0 CMH | 160 mmø | 2.1 m/s | - | 493 | - | 0.44 Pa/m | 0.215 Pa | 196.326 Pa
| Fittings | 150.0 CMH | - | 2.1 m/s | 2.582 Pa | - | 75.9427 | - | 196.111 Pa
| Air Terminal | 150.0 CMH | - | - | - | - | - | - | 0.000 Pa
169 | Duct | 250.0 CMH | 200 mmø | 2.2 m/s | - | 4326 | - | 0.37 Pa/m | 1.605 Pa | 345.672 Pa
| Fittings | 250.0 CMH | - | 2.2 m/s | 2.938 Pa | - | 117.1036 | - | 344.067 Pa
| Air Terminal | 250.0 CMH | - | - | - | - | - | - | 0.000 Pa
170 | Duct | 175.0 CMH | 160 mmø | 2.4 m/s | - | 906 | - | 0.58 Pa/m | 0.522 Pa | 15.987 Pa
| Fittings | 175.0 CMH | - | 2.4 m/s | 3.515 Pa | - | 4.4 | - | 15.465 Pa
| Air Terminal | 175.0 CMH | - | - | - | - | - | - | 0.000 Pa
171 | Duct | 125.0 CMH | 160 mmø | 1.7 m/s | - | 186 | - | 0.32 Pa/m | 0.059 Pa | 8.749 Pa
| Fittings | 125.0 CMH | - | 1.7 m/s | 1.793 Pa | - | 4.8461 | - | 8.691 Pa
| Air Terminal | 125.0 CMH | - | - | - | - | - | - | 0.000 Pa
172 | Duct | 250.0 CMH | 200 mmø | 2.2 m/s | - | 4339 | - | 0.37 Pa/m | 1.609 Pa | 346.381 Pa
| Fittings | 250.0 CMH | - | 2.2 m/s | 2.938 Pa | - | 117.3433 | - | 344.772 Pa
| Air Terminal | 250.0 CMH | - | - | - | - | - | - | 0.000 Pa
173 | Duct | 100.0 CMH | 160 mmø | 1.4 m/s | - | 1285 | - | 0.21 Pa/m | 0.272 Pa | 193.116 Pa
| Fittings | 100.0 CMH | - | 1.4 m/s | 1.148 Pa | - | 168.0239 | - | 192.843 Pa
| Air Terminal | 100.0 CMH | - | - | - | - | - | - | 0.000 Pa
174 | Duct | 600.0 CMH | 250 mmø | 3.4 m/s | - | 5587 | - | 0.61 Pa/m | 3.394 Pa | 3.535 Pa
| Fittings | 600.0 CMH | - | 3.4 m/s | 6.932 Pa | - | 0.020281 | - | 0.141 Pa
175 | Fittings | 600.0 CMH | - | 0.0 m/s | 4.405 Pa | - | 8.7181 | - | 38.406 Pa | 38.406 Pa
176 | Duct | 150.0 CMH | 160 mmø | 2.1 m/s | - | 482 | - | 0.44 Pa/m | 0.210 Pa | 199.782 Pa
| Fittings | 150.0 CMH | - | 2.1 m/s | 2.582 Pa | - | 77.2829 | - | 199.572 Pa
| Air Terminal | 150.0 CMH | - | - | - | - | - | - | 0.000 Pa
177 | Duct | 150.0 CMH | 160 mmø | 2.1 m/s | - | 1442 | - | 0.44 Pa/m | 0.630 Pa | 191.647 Pa
| Fittings | 150.0 CMH | - | 2.1 m/s | 2.582 Pa | - | 73.9703 | - | 191.017 Pa
| Air Terminal | 150.0 CMH | - | - | - | - | - | - | 0.000 Pa
178 | Duct | 500.0 CMH | 250 mmø | 2.8 m/s | - | 2530 | - | 0.44 Pa/m | 1.106 Pa | 192.324 Pa
| Fittings | 500.0 CMH | - | 2.8 m/s | 4.814 Pa | - | 39.7225 | - | 191.218 Pa
179 | Duct | 300.0 CMH | - | 2.7 m/s | - | 222 | - | 0.51 Pa/m | 0.114 Pa | 0.267 Pa
| Fittings | 300.0 CMH | - | 2.7 m/s | 4.231 Pa | - | 0.036 | - | 0.152 Pa
| Air Terminal | 300.0 CMH | - | - | - | - | - | - | 0.000 Pa
180 | Fittings | 300.0 CMH | - | 0.0 m/s | 1.733 Pa | - | 2.9 | - | 5.026 Pa | 5.026 Pa
181 | Duct | 400.0 CMH | 250 mmø | 2.3 m/s | - | 2310 | - | 0.29 Pa/m | 0.676 Pa | 33.930 Pa
| Fittings | 400.0 CMH | - | 2.3 m/s | 3.081 Pa | - | 10.7935 | - | 33.253 Pa
| Air Terminal | 400.0 CMH | - | - | - | - | - | - | 0.000 Pa
182 | Duct | 400.0 CMH | 315 mmø | 1.4 m/s | - | 30 | - | 0.10 Pa/m | 0.003 Pa | 0.003 Pa
| Fittings | 400.0 CMH | - | 1.4 m/s | 1.222 Pa | - | 0 | - | 0.000 Pa
183 | Duct | 1250.0 CMH | 315 mmø | 4.5 m/s | - | 2650 | - | 0.75 Pa/m | 1.975 Pa | 91.032 Pa
| Fittings | 1250.0 CMH | - | 4.5 m/s | 11.937 Pa | - | 7.4607 | - | 89.057 Pa
184 | Duct | 1400.0 CMH | 315 mmø | 5.0 m/s | - | 5223 | - | 0.92 Pa/m | 4.785 Pa | 66.923 Pa
| Fittings | 1400.0 CMH | - | 5.0 m/s | 14.974 Pa | - | 4.1498 | - | 62.138 Pa
185 | Duct | 1550.0 CMH | 315 mmø | 5.5 m/s | - | 9317 | - | 1.10 Pa/m | 10.290 Pa | 189.358 Pa
| Fittings | 1550.0 CMH | - | 5.5 m/s | 18.354 Pa | - | 9.7563 | - | 179.068 Pa
186 | Fittings | 1550.0 CMH | - | 0.0 m/s | 18.559 Pa | - | 1.905 | - | 35.355 Pa | 35.355 Pa
187 | Duct | 150.0 CMH | 160 mmø | 2.1 m/s | - | 3030 | - | 0.44 Pa/m | 1.323 Pa | 203.457 Pa
| Fittings | 150.0 CMH | - | 2.1 m/s | 2.582 Pa | - | 78.2752 | - | 202.134 Pa
| Air Terminal | 150.0 CMH | - | - | - | - | - | - | 0.000 Pa
188 | Duct | 350.0 CMH | 200 mmø | 3.1 m/s | - | 1483 | - | 0.68 Pa/m | 1.007 Pa | 355.638 Pa
| Fittings | 350.0 CMH | - | 3.1 m/s | 5.759 Pa | - | 61.5812 | - | 354.632 Pa
| Air Terminal | 350.0 CMH | - | - | - | - | - | - | 0.000 Pa
189 | Duct | 850.0 CMH | 250 mmø | 4.8 m/s | - | 10515 | - | 1.14 Pa/m | 12.025 Pa | 15.225 Pa
| Fittings | 850.0 CMH | - | 4.8 m/s | 13.912 Pa | - | 0.23002 | - | 3.200 Pa
190 | Duct | 125.0 CMH | 160 mmø | 1.7 m/s | - | 3373 | - | 0.32 Pa/m | 1.064 Pa | 203.356 Pa
| Fittings | 125.0 CMH | - | 1.7 m/s | 1.793 Pa | - | 112.8043 | - | 202.292 Pa
| Air Terminal | 125.0 CMH | - | - | - | - | - | - | 0.000 Pa
191 | Duct | 125.0 CMH | 160 mmø | 1.7 m/s | - | 3412 | - | 0.32 Pa/m | 1.076 Pa | 30.767 Pa
| Fittings | 125.0 CMH | - | 1.7 m/s | 1.793 Pa | - | 16.5564 | - | 29.691 Pa
| Air Terminal | 125.0 CMH | - | - | - | - | - | - | 0.000 Pa
192 | Duct | 250.0 CMH | 160 mmø | 3.5 m/s | - | 2765 | - | 1.09 Pa/m | 3.027 Pa | 184.976 Pa
| Fittings | 250.0 CMH | - | 3.5 m/s | 7.173 Pa | - | 25.3652 | - | 181.950 Pa
193 | Fittings | 250.0 CMH | - | 0.0 m/s | 1.203 Pa | - | 21.4025 | - | 25.757 Pa | 25.757 Pa
194 | Duct | 350.0 CMH | 250 mmø | 2.0 m/s | - | 2539 | - | 0.23 Pa/m | 0.585 Pa | 34.103 Pa
| Fittings | 350.0 CMH | - | 2.0 m/s | 2.359 Pa | - | 14.2095 | - | 33.517 Pa
195 | Duct | 125.0 CMH | 160 mmø | 1.7 m/s | - | 3382 | - | 0.32 Pa/m | 1.067 Pa | 31.557 Pa
| Fittings | 125.0 CMH | - | 1.7 m/s | 1.793 Pa | - | 17.0025 | - | 30.491 Pa
| Air Terminal | 125.0 CMH | - | - | - | - | - | - | 0.000 Pa
196 | Duct | 125.0 CMH | - | 1.7 m/s | - | 263 | - | 0.32 Pa/m | 0.083 Pa | 7.973 Pa
| Fittings | 125.0 CMH | - | 1.7 m/s | 1.793 Pa | - | 4.4 | - | 7.891 Pa
| Air Terminal | 125.0 CMH | - | - | - | - | - | - | 0.000 Pa
197 | Duct | 100.0 CMH | 160 mmø | 1.4 m/s | - | 1285 | - | 0.21 Pa/m | 0.272 Pa | 186.775 Pa
| Fittings | 100.0 CMH | - | 1.4 m/s | 1.148 Pa | - | 162.4994 | - | 186.503 Pa
| Air Terminal | 100.0 CMH | - | - | - | - | - | - | 0.000 Pa
198 | Duct | 100.0 CMH | 160 mmø | 1.4 m/s | - | 392 | - | 0.21 Pa/m | 0.083 Pa | 187.386 Pa
| Fittings | 100.0 CMH | - | 1.4 m/s | 1.148 Pa | - | 163.1964 | - | 187.303 Pa
| Air Terminal | 100.0 CMH | - | - | - | - | - | - | 0.000 Pa
199 | Duct | 150.0 CMH | 160 mmø | 2.1 m/s | - | 826 | - | 0.44 Pa/m | 0.361 Pa | 260.180 Pa
| Fittings | 150.0 CMH | - | 2.1 m/s | 2.582 Pa | - | 100.6134 | - | 259.819 Pa
| Air Terminal | 150.0 CMH | - | - | - | - | - | - | 0.000 Pa
200 | Duct | 125.0 CMH | 160 mmø | 1.7 m/s | - | 915 | - | 0.32 Pa/m | 0.289 Pa | 202.645 Pa
| Fittings | 125.0 CMH | - | 1.7 m/s | 1.793 Pa | - | 112.84 | - | 202.356 Pa
| Air Terminal | 125.0 CMH | - | - | - | - | - | - | 0.000 Pa
201 | Duct | 100.0 CMH | 160 mmø | 1.4 m/s | - | 1757 | - | 0.21 Pa/m | 0.373 Pa | 183.797 Pa
| Fittings | 100.0 CMH | - | 1.4 m/s | 1.148 Pa | - | 159.8179 | - | 183.425 Pa
| Air Terminal | 100.0 CMH | - | - | - | - | - | - | 0.000 Pa
202 | Duct | 100.0 CMH | 160 mmø | 1.4 m/s | - | 1757 | - | 0.21 Pa/m | 0.372 Pa | 185.187 Pa
| Fittings | 100.0 CMH | - | 1.4 m/s | 1.148 Pa | - | 161.0287 | - | 184.815 Pa
| Air Terminal | 100.0 CMH | - | - | - | - | - | - | 0.000 Pa
203 | Duct | 100.0 CMH | 160 mmø | 1.4 m/s | - | 1757 | - | 0.21 Pa/m | 0.373 Pa | 187.374 Pa
| Fittings | 100.0 CMH | - | 1.4 m/s | 1.148 Pa | - | 162.9344 | - | 187.002 Pa
| Air Terminal | 100.0 CMH | - | - | - | - | - | - | 0.000 Pa
204 | Duct | 100.0 CMH | 160 mmø | 1.4 m/s | - | 1896 | - | 0.21 Pa/m | 0.402 Pa | 182.002 Pa
| Fittings | 100.0 CMH | - | 1.4 m/s | 1.148 Pa | - | 158.2278 | - | 181.600 Pa
| Air Terminal | 100.0 CMH | - | - | - | - | - | - | 0.000 Pa
205 | Duct | 250.0 CMH | 250 mmø | 1.4 m/s | - | 484 | - | 0.13 Pa/m | 0.061 Pa | 6.956 Pa
| Fittings | 250.0 CMH | - | 1.4 m/s | 1.203 Pa | - | 5.7295 | - | 6.895 Pa
| Air Terminal | 250.0 CMH | - | - | - | - | - | - | 0.000 Pa
206 | Duct | 500.0 CMH | 250 mmø | 2.8 m/s | - | 2098 | - | 0.44 Pa/m | 0.917 Pa | 75.797 Pa
| Fittings | 500.0 CMH | - | 2.8 m/s | 4.814 Pa | - | 15.5551 | - | 74.880 Pa
207 | Duct | 250.0 CMH | 250 mmø | 1.4 m/s | - | 2902 | - | 0.13 Pa/m | 0.367 Pa | 28.263 Pa
| Fittings | 250.0 CMH | - | 1.4 m/s | 1.203 Pa | - | 23.1791 | - | 27.895 Pa
| Air Terminal | 250.0 CMH | - | - | - | - | - | - | 0.000 Pa
208 | Duct | 100.0 CMH | 160 mmø | 1.4 m/s | - | 2235 | - | 0.21 Pa/m | 0.474 Pa | 182.874 Pa
| Fittings | 100.0 CMH | - | 1.4 m/s | 1.148 Pa | - | 158.9248 | - | 182.400 Pa
| Air Terminal | 100.0 CMH | - | - | - | - | - | - | 0.000 Pa
209 | Duct | 100.0 CMH | 200 mmx200 mm | 0.7 m/s | - | 385 | - | 0.05 Pa/m | 0.018 Pa | 0.018 Pa
| Fittings | 100.0 CMH | - | 0.7 m/s | 0.290 Pa | - | 0 | - | 0.000 Pa
Critical Path : 11-10-21-20-19-18-147-146-165-164-163-162-161-186-185-184-183-189-188 ; Total Pressure Loss : 925.403 Pa
Detail Information of Straight Segment by Sections
Section | Element ID | Flow | Size | Velocity | Velocity Pressure | Length | Pressure Loss | Total Pressure Loss
1 | 173899 | 250.0 CMH | 250 mmø | 1.4 m/s | 1.203 Pa | 112 | 0.014 Pa | 0.014 Pa
2 | 173554 | 500.0 CMH | 250 mmø | 2.8 m/s | 4.814 Pa | 554 | 0.242 Pa | 1.993 Pa
| 174637 | 500.0 CMH | 250 mmø | 2.8 m/s | 4.814 Pa | 1626 | 0.711 Pa
| 174925 | 500.0 CMH | 250 mmø | 2.8 m/s | 4.814 Pa | 624 | 0.273 Pa
| 175450 | 500.0 CMH | 250 mmø | 2.8 m/s | 4.814 Pa | 687 | 0.300 Pa
| 176062 | 500.0 CMH | 250 mmø | 2.8 m/s | 4.814 Pa | 548 | 0.239 Pa
| 176074 | 500.0 CMH | 250 mmø | 2.8 m/s | 4.814 Pa | 271 | 0.118 Pa
| 176314 | 500.0 CMH | 250 mmø | 2.8 m/s | 4.814 Pa | 250 | 0.109 Pa
3 | 172909 | 650.0 CMH | 250 mmø | 3.7 m/s | 8.135 Pa | 779 | 0.547 Pa | 4.379 Pa
| 173383 | 650.0 CMH | 250 mmø | 3.7 m/s | 8.135 Pa | 3707 | 2.603 Pa
| 173662 | 650.0 CMH | 250 mmø | 3.7 m/s | 8.135 Pa | 648 | 0.455 Pa
| 174577 | 650.0 CMH | 250 mmø | 3.7 m/s | 8.135 Pa | 606 | 0.426 Pa
| 174589 | 650.0 CMH | 250 mmø | 3.7 m/s | 8.135 Pa | 408 | 0.286 Pa
| 2304998 | 650.0 CMH | 250 mmø | 3.7 m/s | 8.135 Pa | 90 | 0.063 Pa
4 | 190772 | 2099.8 CMH | 400 mmx400 mm | 3.6 m/s | 7.991 Pa | 200 | 0.077 Pa | 0.163 Pa
| 194754 | 2099.8 CMH | 400 mmx400 mm | 3.6 m/s | 7.991 Pa | 224 | 0.086 Pa
5 | 193210 | 2099.8 CMH | 400 mmx400 mm | 3.6 m/s | 7.991 Pa | 1188 | 0.456 Pa | 0.456 Pa
6 | 191022 | 2349.8 CMH | 400 mmx400 mm | 4.1 m/s | 10.007 Pa | 1417 | 0.667 Pa | 3.016 Pa
| 191150 | 2349.8 CMH | 400 mmx400 mm | 4.1 m/s | 10.007 Pa | 1500 | 0.706 Pa
| 193210 | 2349.8 CMH | 400 mmx400 mm | 4.1 m/s | 10.007 Pa | 312 | 0.147 Pa
| 194830 | 2349.8 CMH | 400 mmx400 mm | 4.1 m/s | 10.007 Pa | 1500 | 0.706 Pa
| 195232 | 2349.8 CMH | 400 mmx400 mm | 4.1 m/s | 10.007 Pa | 978 | 0.460 Pa
| 195274 | 2349.8 CMH | 400 mmx400 mm | 4.1 m/s | 10.007 Pa | 700 | 0.330 Pa
7 | 194392 | 3299.8 CMH | 500 mmx500 mm | 3.7 m/s | 8.083 Pa | 619 | 0.182 Pa | 0.563 Pa
| 194674 | 3299.8 CMH | 500 mmx500 mm | 3.7 m/s | 8.083 Pa | 1300 | 0.382 Pa
8 | 190214 | 3299.8 CMH | 600 mmx600 mm | 2.5 m/s | 3.898 Pa | 911 | 0.110 Pa | 0.231 Pa
| 195522 | 3299.8 CMH | 600 mmx600 mm | 2.5 m/s | 3.898 Pa | 1000 | 0.121 Pa
9 | 190214 | 5399.6 CMH | 600 mmx600 mm | 4.2 m/s | 10.438 Pa | 589 | 0.176 Pa | 4.614 Pa
| 191312 | 5399.6 CMH | 600 mmx600 mm | 4.2 m/s | 10.438 Pa | 1400 | 0.419 Pa
| 191480 | 5399.6 CMH | 600 mmx600 mm | 4.2 m/s | 10.438 Pa | 852 | 0.255 Pa
| 191864 | 5399.6 CMH | 600 mmx600 mm | 4.2 m/s | 10.438 Pa | 1500 | 0.449 Pa
| 191998 | 5399.6 CMH | 600 mmx600 mm | 4.2 m/s | 10.438 Pa | 468 | 0.140 Pa
| 192084 | 5399.6 CMH | 600 mmx600 mm | 4.2 m/s | 10.438 Pa | 404 | 0.121 Pa
| 192136 | 5399.6 CMH | 600 mmx600 mm | 4.2 m/s | 10.438 Pa | 1500 | 0.449 Pa
| 192314 | 5399.6 CMH | 600 mmx600 mm | 4.2 m/s | 10.438 Pa | 1500 | 0.449 Pa
| 192580 | 5399.6 CMH | 600 mmx600 mm | 4.2 m/s | 10.438 Pa | 87 | 0.026 Pa
| 192658 | 5399.6 CMH | 600 mmx600 mm | 4.2 m/s | 10.438 Pa | 752 | 0.225 Pa
| 192702 | 5399.6 CMH | 600 mmx600 mm | 4.2 m/s | 10.438 Pa | 1300 | 0.389 Pa
| 193002 | 5399.6 CMH | 600 mmx600 mm | 4.2 m/s | 10.438 Pa | 719 | 0.215 Pa
| 193036 | 5399.6 CMH | 600 mmx600 mm | 4.2 m/s | 10.438 Pa | 1200 | 0.359 Pa
| 193560 | 5399.6 CMH | 600 mmx600 mm | 4.2 m/s | 10.438 Pa | 1500 | 0.449 Pa
| 193568 | 5399.6 CMH | 600 mmx600 mm | 4.2 m/s | 10.438 Pa | 86 | 0.026 Pa
| 193580 | 5399.6 CMH | 600 mmx600 mm | 4.2 m/s | 10.438 Pa | 564 | 0.169 Pa
| 193818 | 5399.6 CMH | 600 mmx600 mm | 4.2 m/s | 10.438 Pa | 1000 | 0.299 Pa
10 | 191342 | 12699.6 CMH | 1000 mmx1000 mm | 3.5 m/s | 7.483 Pa | 1500 | 0.178 Pa | 2.813 Pa
| 191414 | 12699.6 CMH | 1000 mmx1000 mm | 3.5 m/s | 7.483 Pa | 1500 | 0.178 Pa
| 191520 | 12699.6 CMH | 1000 mmx1000 mm | 3.5 m/s | 7.483 Pa | 390 | 0.046 Pa
| 191586 | 12699.6 CMH | 1000 mmx1000 mm | 3.5 m/s | 7.483 Pa | 182 | 0.022 Pa
| 191664 | 12699.6 CMH | 1000 mmx1000 mm | 3.5 m/s | 7.483 Pa | 740 | 0.088 Pa
| 191714 | 12699.6 CMH | 1000 mmx1000 mm | 3.5 m/s | 7.483 Pa | 1012 | 0.120 Pa
| 191718 | 12699.6 CMH | 1000 mmx1000 mm | 3.5 m/s | 7.483 Pa | 1500 | 0.178 Pa
| 191750 | 12699.6 CMH | 1000 mmx1000 mm | 3.5 m/s | 7.483 Pa | 1500 | 0.178 Pa
| 192330 | 12699.6 CMH | 1000 mmx1000 mm | 3.5 m/s | 7.483 Pa | 1500 | 0.178 Pa
| 192542 | 12699.6 CMH | 1000 mmx1000 mm | 3.5 m/s | 7.483 Pa | 680 | 0.081 Pa
| 192634 | 12699.6 CMH | 1000 mmx1000 mm | 3.5 m/s | 7.483 Pa | 1500 | 0.178 Pa
| 193080 | 12699.6 CMH | 1000 mmx1000 mm | 3.5 m/s | 7.483 Pa | 323 | 0.038 Pa
| 193152 | 12699.6 CMH | 1000 mmx1000 mm | 3.5 m/s | 7.483 Pa | 1500 | 0.178 Pa
| 193570 | 12699.6 CMH | 1000 mmx1000 mm | 3.5 m/s | 7.483 Pa | 1500 | 0.178 Pa
| 193826 | 12699.6 CMH | 1000 mmx1000 mm | 3.5 m/s | 7.483 Pa | 1858 | 0.221 Pa
| 194142 | 12699.6 CMH | 1000 mmx1000 mm | 3.5 m/s | 7.483 Pa | 1500 | 0.178 Pa
| 194202 | 12699.6 CMH | 1000 mmx1000 mm | 3.5 m/s | 7.483 Pa | 1500 | 0.178 Pa
| 194310 | 12699.6 CMH | 1000 mmx1000 mm | 3.5 m/s | 7.483 Pa | 1500 | 0.178 Pa
| 194334 | 12699.6 CMH | 1000 mmx1000 mm | 3.5 m/s | 7.483 Pa | 496 | 0.059 Pa
| 194424 | 12699.6 CMH | 1000 mmx1000 mm | 3.5 m/s | 7.483 Pa | 1500 | 0.178 Pa
12 | 175141 | 250.0 CMH | 250 mmø | 1.4 m/s | 1.203 Pa | 2540 | 0.321 Pa | 0.336 Pa
| 175348 | 250.0 CMH | 250 mmø | 1.4 m/s | 1.203 Pa | 112 | 0.014 Pa
13 | 161149 | 200.0 CMH | 160 mmø | 2.8 m/s | 4.591 Pa | 80 | 0.059 Pa | 0.364 Pa
| 161290 | 200.0 CMH | 160 mmø | 2.8 m/s | 4.591 Pa | 298 | 0.218 Pa
| 162121 | 200.0 CMH | 160 mmø | 2.8 m/s | 4.591 Pa | 53 | 0.039 Pa
| 162481 | 200.0 CMH | 160 mmø | 2.8 m/s | 4.591 Pa | 67 | 0.049 Pa
14 | 160861 | 1150.0 CMH | 280 mmø | 5.2 m/s | 16.184 Pa | 375 | 0.428 Pa | 11.338 Pa
| 161557 | 1150.0 CMH | 280 mmø | 5.2 m/s | 16.184 Pa | 2189 | 2.494 Pa
| 162805 | 1150.0 CMH | 280 mmø | 5.2 m/s | 16.184 Pa | 5524 | 6.295 Pa
| 2159405 | 1150.0 CMH | 280 mmø | 5.2 m/s | 16.184 Pa | 134 | 0.152 Pa
| 2159426 | 1150.0 CMH | 280 mmø | 5.2 m/s | 16.184 Pa | 57 | 0.065 Pa
| 2159427 | 1150.0 CMH | 280 mmø | 5.2 m/s | 16.184 Pa | 393 | 0.447 Pa
| 2159474 | 1150.0 CMH | 280 mmø | 5.2 m/s | 16.184 Pa | 576 | 0.657 Pa
| 2159489 | 1150.0 CMH | 280 mmø | 5.2 m/s | 16.184 Pa | 701 | 0.799 Pa
15 | 191300 | 2300.0 CMH | 400 mmx400 mm | 4.0 m/s | 9.588 Pa | 45 | 0.020 Pa | 1.174 Pa
| 191318 | 2300.0 CMH | 400 mmx400 mm | 4.0 m/s | 9.588 Pa | 271 | 0.123 Pa
| 191500 | 2300.0 CMH | 400 mmx400 mm | 4.0 m/s | 9.588 Pa | 845 | 0.383 Pa
| 192410 | 2300.0 CMH | 400 mmx400 mm | 4.0 m/s | 9.588 Pa | 200 | 0.091 Pa
| 193294 | 2300.0 CMH | 400 mmx400 mm | 4.0 m/s | 9.588 Pa | 78 | 0.035 Pa
| 194858 | 2300.0 CMH | 400 mmx400 mm | 4.0 m/s | 9.588 Pa | 1153 | 0.522 Pa
16 | 189862 | 2300.0 CMH | 450 mmx450 mm | 3.2 m/s | 5.985 Pa | 1172 | 0.299 Pa | 0.299 Pa
17 | 189862 | 2550.0 CMH | 450 mmx450 mm | 3.5 m/s | 7.357 Pa | 302 | 0.093 Pa | 0.308 Pa
| 195382 | 2550.0 CMH | 450 mmx450 mm | 3.5 m/s | 7.357 Pa | 699 | 0.215 Pa
18 | 192162 | 7300.0 CMH | 700 mmx700 mm | 4.1 m/s | 10.298 Pa | 1500 | 0.368 Pa | 1.946 Pa
| 192474 | 7300.0 CMH | 700 mmx700 mm | 4.1 m/s | 10.298 Pa | 990 | 0.243 Pa
| 193230 | 7300.0 CMH | 700 mmx700 mm | 4.1 m/s | 10.298 Pa | 200 | 0.049 Pa
| 193494 | 7300.0 CMH | 700 mmx700 mm | 4.1 m/s | 10.298 Pa | 600 | 0.147 Pa
| 193532 | 7300.0 CMH | 700 mmx700 mm | 4.1 m/s | 10.298 Pa | 1500 | 0.368 Pa
| 194180 | 7300.0 CMH | 700 mmx700 mm | 4.1 m/s | 10.298 Pa | 1500 | 0.368 Pa
| 194396 | 7300.0 CMH | 700 mmx700 mm | 4.1 m/s | 10.298 Pa | 1000 | 0.245 Pa
| 194954 | 7300.0 CMH | 700 mmx700 mm | 4.1 m/s | 10.298 Pa | 645 | 0.158 Pa
19 | 191404 | 7300.0 CMH | 1000 mmx500 mm | 4.1 m/s | 9.890 Pa | 663 | 0.166 Pa | 2.613 Pa
| 191468 | 7300.0 CMH | 1000 mmx500 mm | 4.1 m/s | 9.890 Pa | 374 | 0.094 Pa
| 192218 | 7300.0 CMH | 1000 mmx500 mm | 4.1 m/s | 9.890 Pa | 1500 | 0.376 Pa
| 192716 | 7300.0 CMH | 1000 mmx500 mm | 4.1 m/s | 9.890 Pa | 725 | 0.182 Pa
| 193016 | 7300.0 CMH | 1000 mmx500 mm | 4.1 m/s | 9.890 Pa | 1500 | 0.376 Pa
| 193272 | 7300.0 CMH | 1000 mmx500 mm | 4.1 m/s | 9.890 Pa | 1500 | 0.376 Pa
| 193386 | 7300.0 CMH | 1000 mmx500 mm | 4.1 m/s | 9.890 Pa | 912 | 0.229 Pa
| 193438 | 7300.0 CMH | 1000 mmx500 mm | 4.1 m/s | 9.890 Pa | 1200 | 0.301 Pa
| 193578 | 7300.0 CMH | 1000 mmx500 mm | 4.1 m/s | 9.890 Pa | 550 | 0.138 Pa
| 194322 | 7300.0 CMH | 1000 mmx500 mm | 4.1 m/s | 9.890 Pa | 1500 | 0.376 Pa
20 | 192062 | 7300.0 CMH | 1000 mmx500 mm | 4.1 m/s | 9.890 Pa | 700 | 0.175 Pa | 1.409 Pa
| 192392 | 7300.0 CMH | 1000 mmx500 mm | 4.1 m/s | 9.890 Pa | 1285 | 0.322 Pa
| 193322 | 7300.0 CMH | 1000 mmx500 mm | 4.1 m/s | 9.890 Pa | 1500 | 0.376 Pa
| 193352 | 7300.0 CMH | 1000 mmx500 mm | 4.1 m/s | 9.890 Pa | 800 | 0.200 Pa
| 194058 | 7300.0 CMH | 1000 mmx500 mm | 4.1 m/s | 9.890 Pa | 1338 | 0.335 Pa
21 | 191714 | 7300.0 CMH | 1000 mmx1000 mm | 2.0 m/s | 2.473 Pa | 488 | 0.021 Pa | 0.055 Pa
| 192694 | 7300.0 CMH | 1000 mmx1000 mm | 2.0 m/s | 2.473 Pa | 800 | 0.034 Pa
22 | 157696 | 100.0 CMH | 160 mmø | 1.4 m/s | 1.148 Pa | 115 | 0.024 Pa | 0.540 Pa
| 159202 | 100.0 CMH | 160 mmø | 1.4 m/s | 1.148 Pa | 425 | 0.090 Pa
| 461492 | 100.0 CMH | 160 mm | 1.4 m/s | 1.148 Pa | 261 | 0.055 Pa
| 2174104 | 100.0 CMH | 160 mmø | 1.4 m/s | 1.148 Pa | 947 | 0.201 Pa
| 2174113 | 100.0 CMH | 160 mmø | 1.4 m/s | 1.148 Pa | 800 | 0.170 Pa
23 | 190246 | 400.0 CMH | 200 mmx200 mm | 2.8 m/s | 4.640 Pa | 752 | 0.421 Pa | 1.902 Pa
| 192284 | 400.0 CMH | 200 mmx200 mm | 2.8 m/s | 4.640 Pa | 1500 | 0.838 Pa
| 195520 | 400.0 CMH | 200 mmx200 mm | 2.8 m/s | 4.640 Pa | 1151 | 0.643 Pa
24 | 190056 | 500.0 CMH | 200 mmx200 mm | 3.5 m/s | 7.250 Pa | 422 | 0.353 Pa | 1.183 Pa
| 193822 | 500.0 CMH | 200 mmx200 mm | 3.5 m/s | 7.250 Pa | 813 | 0.680 Pa
| 195520 | 500.0 CMH | 200 mmx200 mm | 3.5 m/s | 7.250 Pa | 179 | 0.150 Pa
25 | 192324 | 500.0 CMH | 200 mmx200 mm | 3.5 m/s | 7.250 Pa | 474 | 0.397 Pa | 0.495 Pa
| 893555 | 500.0 CMH | 200 mmx200 mm | 3.5 m/s | 7.250 Pa | 117 | 0.098 Pa
27 | 192982 | 500.0 CMH | 200 mmx200 mm | 3.5 m/s | 7.250 Pa | 391 | 0.327 Pa | 0.849 Pa
| 894029 | 500.0 CMH | 200 mmx200 mm | 3.5 m/s | 7.250 Pa | 625 | 0.523 Pa
28 | 190442 | 950.0 CMH | 300 mmx200 mm | 4.4 m/s | 11.632 Pa | 161 | 0.165 Pa | 0.165 Pa
29 | 190776 | 950.0 CMH | 300 mmx200 mm | 4.4 m/s | 11.632 Pa | 134 | 0.137 Pa | 0.137 Pa
30 | 194582 | 950.0 CMH | 300 mmx200 mm | 4.4 m/s | 11.632 Pa | 464 | 0.474 Pa | 0.474 Pa
31 | 190008 | 950.0 CMH | 300 mmx200 mm | 4.4 m/s | 11.632 Pa | 323 | 0.331 Pa | 9.102 Pa
| 190166 | 950.0 CMH | 300 mmx200 mm | 4.4 m/s | 11.632 Pa | 1500 | 1.533 Pa
| 190548 | 950.0 CMH | 300 mmx200 mm | 4.4 m/s | 11.632 Pa | 1519 | 1.553 Pa
| 193004 | 950.0 CMH | 300 mmx200 mm | 4.4 m/s | 11.632 Pa | 1500 | 1.533 Pa
| 193266 | 950.0 CMH | 300 mmx200 mm | 4.4 m/s | 11.632 Pa | 1800 | 1.840 Pa
| 194482 | 950.0 CMH | 300 mmx200 mm | 4.4 m/s | 11.632 Pa | 760 | 0.777 Pa
| 195122 | 950.0 CMH | 300 mmx200 mm | 4.4 m/s | 11.632 Pa | 1500 | 1.533 Pa
32 | 189496 | 950.0 CMH | 350 mmx200 mm | 3.8 m/s | 8.546 Pa | 277 | 0.199 Pa | 1.724 Pa
| 190154 | 950.0 CMH | 350 mmx200 mm | 3.8 m/s | 8.546 Pa | 916 | 0.658 Pa
| 191146 | 950.0 CMH | 350 mmx200 mm | 3.8 m/s | 8.546 Pa | 1000 | 0.718 Pa
| 1619179 | 950.0 CMH | 350 mmx200 mm | 3.8 m/s | 8.546 Pa | 209 | 0.150 Pa
34 | 189972 | 950.0 CMH | 300 mmx200 mm | 4.4 m/s | 11.632 Pa | 683 | 0.698 Pa | 3.543 Pa
| 190238 | 950.0 CMH | 300 mmx200 mm | 4.4 m/s | 11.632 Pa | 437 | 0.446 Pa
| 191424 | 950.0 CMH | 300 mmx200 mm | 4.4 m/s | 11.632 Pa | 797 | 0.814 Pa
| 194082 | 950.0 CMH | 300 mmx200 mm | 4.4 m/s | 11.632 Pa | 1550 | 1.585 Pa
35 | 190204 | 950.0 CMH | 400 mmx300 mm | 2.2 m/s | 2.908 Pa | 800 | 0.150 Pa | 0.594 Pa
| 190260 | 950.0 CMH | 400 mmx300 mm | 2.2 m/s | 2.908 Pa | 443 | 0.083 Pa
| 190418 | 950.0 CMH | 400 mmx300 mm | 2.2 m/s | 2.908 Pa | 88 | 0.017 Pa
| 192690 | 950.0 CMH | 400 mmx300 mm | 2.2 m/s | 2.908 Pa | 1371 | 0.257 Pa
| 194046 | 950.0 CMH | 400 mmx300 mm | 2.2 m/s | 2.908 Pa | 131 | 0.025 Pa
| 195518 | 950.0 CMH | 400 mmx300 mm | 2.2 m/s | 2.908 Pa | 337 | 0.063 Pa
36 | 192184 | 950.0 CMH | 350 mmx350 mm | 2.2 m/s | 2.790 Pa | 1259 | 0.222 Pa | 0.614 Pa
| 192312 | 950.0 CMH | 350 mmx350 mm | 2.2 m/s | 2.790 Pa | 664 | 0.117 Pa
| 192706 | 950.0 CMH | 350 mmx350 mm | 2.2 m/s | 2.790 Pa | 266 | 0.047 Pa
| 193928 | 950.0 CMH | 350 mmx350 mm | 2.2 m/s | 2.790 Pa | 1300 | 0.229 Pa
37 | 194160 | 950.0 CMH | 500 mmx500 mm | 1.1 m/s | 0.670 Pa | 477 | 0.015 Pa | 0.060 Pa
| 194340 | 950.0 CMH | 500 mmx500 mm | 1.1 m/s | 0.670 Pa | 1200 | 0.038 Pa
| 194392 | 950.0 CMH | 500 mmx500 mm | 1.1 m/s | 0.670 Pa | 204 | 0.006 Pa
38 | 161356 | 100.0 CMH | 160 mmø | 1.4 m/s | 1.148 Pa | 520 | 0.110 Pa | 0.402 Pa
| 161491 | 100.0 CMH | 160 mmø | 1.4 m/s | 1.148 Pa | 994 | 0.211 Pa
| 163324 | 100.0 CMH | 160 mmø | 1.4 m/s | 1.148 Pa | 115 | 0.024 Pa
| 1734199 | 100.0 CMH | 160 mm | 1.4 m/s | 1.148 Pa | 269 | 0.057 Pa
39 | 190432 | 500.0 CMH | 200 mmx200 mm | 3.5 m/s | 7.250 Pa | 179 | 0.150 Pa | 2.515 Pa
| 190682 | 500.0 CMH | 200 mmx200 mm | 3.5 m/s | 7.250 Pa | 1312 | 1.097 Pa
| 192942 | 500.0 CMH | 200 mmx200 mm | 3.5 m/s | 7.250 Pa | 422 | 0.353 Pa
| 195448 | 500.0 CMH | 200 mmx200 mm | 3.5 m/s | 7.250 Pa | 1095 | 0.915 Pa
42 | 189456 | 500.0 CMH | 200 mmx200 mm | 3.5 m/s | 7.250 Pa | 425 | 0.355 Pa | 0.471 Pa
| 190828 | 500.0 CMH | 200 mmx200 mm | 3.5 m/s | 7.250 Pa | 138 | 0.115 Pa
43 | 191956 | 1299.8 CMH | 300 mmx300 mm | 4.0 m/s | 9.677 Pa | 454 | 0.297 Pa | 0.297 Pa
44 | 189700 | 1449.8 CMH | 300 mmx300 mm | 4.5 m/s | 12.040 Pa | 1550 | 1.237 Pa | 12.293 Pa
| 190768 | 1449.8 CMH | 300 mmx300 mm | 4.5 m/s | 12.040 Pa | 1500 | 1.197 Pa
| 191212 | 1449.8 CMH | 300 mmx300 mm | 4.5 m/s | 12.040 Pa | 1313 | 1.048 Pa
| 191348 | 1449.8 CMH | 300 mmx300 mm | 4.5 m/s | 12.040 Pa | 1500 | 1.197 Pa
| 191684 | 1449.8 CMH | 300 mmx300 mm | 4.5 m/s | 12.040 Pa | 1500 | 1.197 Pa
| 191780 | 1449.8 CMH | 300 mmx300 mm | 4.5 m/s | 12.040 Pa | 734 | 0.586 Pa
| 191818 | 1449.8 CMH | 300 mmx300 mm | 4.5 m/s | 12.040 Pa | 1500 | 1.197 Pa
| 191956 | 1449.8 CMH | 300 mmx300 mm | 4.5 m/s | 12.040 Pa | 308 | 0.246 Pa
| 192664 | 1449.8 CMH | 300 mmx300 mm | 4.5 m/s | 12.040 Pa | 487 | 0.389 Pa
| 193014 | 1449.8 CMH | 300 mmx300 mm | 4.5 m/s | 12.040 Pa | 150 | 0.120 Pa
| 193140 | 1449.8 CMH | 300 mmx300 mm | 4.5 m/s | 12.040 Pa | 361 | 0.288 Pa
| 2150306 | 1449.8 CMH | 300 mmx300 mm | 4.5 m/s | 12.040 Pa | 1500 | 1.197 Pa
| 2158007 | 1449.8 CMH | 300 mmx300 mm | 4.5 m/s | 12.040 Pa | 1500 | 1.197 Pa
| 2158119 | 1449.8 CMH | 300 mmx300 mm | 4.5 m/s | 12.040 Pa | 1500 | 1.197 Pa
45 | 189786 | 1449.8 CMH | 400 mmx400 mm | 2.5 m/s | 3.810 Pa | 150 | 0.030 Pa | 0.111 Pa
| 195350 | 1449.8 CMH | 400 mmx400 mm | 2.5 m/s | 3.810 Pa | 416 | 0.082 Pa
46 | 193608 | 1849.8 CMH | 400 mmx400 mm | 3.2 m/s | 6.202 Pa | 1188 | 0.363 Pa | 0.602 Pa
| 195350 | 1849.8 CMH | 400 mmx400 mm | 3.2 m/s | 6.202 Pa | 784 | 0.239 Pa
47 | 190738 | 2099.8 CMH | 400 mmx400 mm | 3.6 m/s | 7.991 Pa | 1678 | 0.644 Pa | 2.421 Pa
| 191032 | 2099.8 CMH | 400 mmx400 mm | 3.6 m/s | 7.991 Pa | 1317 | 0.505 Pa
| 193608 | 2099.8 CMH | 400 mmx400 mm | 3.6 m/s | 7.991 Pa | 312 | 0.120 Pa
| 193962 | 2099.8 CMH | 400 mmx400 mm | 3.6 m/s | 7.991 Pa | 1500 | 0.576 Pa
| 194730 | 2099.8 CMH | 400 mmx400 mm | 3.6 m/s | 7.991 Pa | 1500 | 0.576 Pa
48 | 159982 | 150.0 CMH | 160 mmø | 2.1 m/s | 2.582 Pa | 639 | 0.279 Pa | 0.595 Pa
| 161629 | 150.0 CMH | 160 mmø | 2.1 m/s | 2.582 Pa | 444 | 0.194 Pa
| 162061 | 150.0 CMH | 160 mmø | 2.1 m/s | 2.582 Pa | 205 | 0.089 Pa
| 2158374 | 150.0 CMH | 160 mmø | 2.1 m/s | 2.582 Pa | 75 | 0.033 Pa
49 | 160240 | 100.0 CMH | 160 mmø | 1.4 m/s | 1.148 Pa | 163 | 0.035 Pa | 0.082 Pa
| 161623 | 100.0 CMH | 160 mmø | 1.4 m/s | 1.148 Pa | 20 | 0.004 Pa
| 162766 | 100.0 CMH | 160 mmø | 1.4 m/s | 1.148 Pa | 176 | 0.037 Pa
| 163039 | 100.0 CMH | 160 mmø | 1.4 m/s | 1.148 Pa | 27 | 0.006 Pa
50 | 2290759 | 600.0 CMH | 250 mmø | 3.4 m/s | 6.932 Pa | 3190 | 1.938 Pa | 1.938 Pa
51 | 2289990 | 750.0 CMH | 250 mmø | 4.2 m/s | 10.831 Pa | 3190 | 2.904 Pa | 2.904 Pa
53 | 191010 | 850.0 CMH | 300 mmx300 mm | 2.6 m/s | 4.139 Pa | 1320 | 0.401 Pa | 0.857 Pa
| 191370 | 850.0 CMH | 300 mmx300 mm | 2.6 m/s | 4.139 Pa | 1500 | 0.456 Pa
54 | 190670 | 1000.0 CMH | 300 mmx300 mm | 3.1 m/s | 5.728 Pa | 491 | 0.200 Pa | 0.273 Pa
| 191010 | 1000.0 CMH | 300 mmx300 mm | 3.1 m/s | 5.728 Pa | 180 | 0.073 Pa
55 | 190670 | 1150.0 CMH | 300 mmx300 mm | 3.5 m/s | 7.575 Pa | 1009 | 0.529 Pa | 1.105 Pa
| 191432 | 1150.0 CMH | 300 mmx300 mm | 3.5 m/s | 7.575 Pa | 1099 | 0.576 Pa
57 | 194548 | 1150.0 CMH | 350 mmx200 mm | 4.6 m/s | 12.523 Pa | 500 | 0.508 Pa | 0.508 Pa
58 | 190676 | 1150.0 CMH | 350 mmx200 mm | 4.6 m/s | 12.523 Pa | 700 | 0.711 Pa | 2.235 Pa
| 192154 | 1150.0 CMH | 350 mmx200 mm | 4.6 m/s | 12.523 Pa | 1500 | 1.524 Pa
59 | 189528 | 1150.0 CMH | 400 mmx400 mm | 2.0 m/s | 2.397 Pa | 92 | 0.012 Pa | 0.068 Pa
| 192378 | 1150.0 CMH | 400 mmx400 mm | 2.0 m/s | 2.397 Pa | 101 | 0.013 Pa
| 192410 | 1150.0 CMH | 400 mmx400 mm | 2.0 m/s | 2.397 Pa | 200 | 0.026 Pa
| 194360 | 1150.0 CMH | 400 mmx400 mm | 2.0 m/s | 2.397 Pa | 127 | 0.017 Pa
60 | 156433 | 150.0 CMH | 160 mmø | 2.1 m/s | 2.582 Pa | 181 | 0.079 Pa | 0.267 Pa
| 157195 | 150.0 CMH | 160 mmø | 2.1 m/s | 2.582 Pa | 194 | 0.085 Pa
| 1269024 | 150.0 CMH | 160 mmø | 2.1 m/s | 2.582 Pa | 235 | 0.103 Pa
61 | 156367 | 300.0 CMH | 160 mmø | 4.1 m/s | 10.329 Pa | 451 | 0.686 Pa | 22.560 Pa
| 156592 | 300.0 CMH | 160 mmø | 4.1 m/s | 10.329 Pa | 3330 | 5.073 Pa
| 157702 | 300.0 CMH | 160 mmø | 4.1 m/s | 10.329 Pa | 2823 | 4.300 Pa
| 157774 | 300.0 CMH | 160 mmø | 4.1 m/s | 10.329 Pa | 175 | 0.267 Pa
| 157843 | 300.0 CMH | 160 mmø | 4.1 m/s | 10.329 Pa | 418 | 0.637 Pa
| 157888 | 300.0 CMH | 160 mmø | 4.1 m/s | 10.329 Pa | 565 | 0.861 Pa
| 158320 | 300.0 CMH | 160 mmø | 4.1 m/s | 10.329 Pa | 2135 | 3.252 Pa
| 159559 | 300.0 CMH | 160 mmø | 4.1 m/s | 10.329 Pa | 259 | 0.395 Pa
| 390938 | 300.0 CMH | 160 mmø | 4.1 m/s | 10.329 Pa | 939 | 1.430 Pa
| 962979 | 300.0 CMH | 160 mmø | 4.1 m/s | 10.329 Pa | 3576 | 5.447 Pa
| 1268967 | 300.0 CMH | 160 mmø | 4.1 m/s | 10.329 Pa | 139 | 0.212 Pa
63 | 190442 | 300.0 CMH | 300 mmx200 mm | 1.4 m/s | 1.160 Pa | 439 | 0.057 Pa | 0.057 Pa
64 | 190442 | 450.0 CMH | 300 mmx200 mm | 2.1 m/s | 2.610 Pa | 0 | 0.000 Pa | 0.000 Pa
65 | 161422 | 100.0 CMH | 160 mmø | 1.4 m/s | 1.148 Pa | 115 | 0.024 Pa | 0.372 Pa
| 163135 | 100.0 CMH | 160 mmø | 1.4 m/s | 1.148 Pa | 947 | 0.201 Pa
| 163429 | 100.0 CMH | 160 mmø | 1.4 m/s | 1.148 Pa | 425 | 0.090 Pa
| 1734195 | 100.0 CMH | 160 mm | 1.4 m/s | 1.148 Pa | 269 | 0.057 Pa
66 | 190432 | 400.0 CMH | 200 mmx200 mm | 2.8 m/s | 4.640 Pa | 1151 | 0.643 Pa | 1.902 Pa
| 191206 | 400.0 CMH | 200 mmx200 mm | 2.8 m/s | 4.640 Pa | 1500 | 0.838 Pa
| 193124 | 400.0 CMH | 200 mmx200 mm | 2.8 m/s | 4.640 Pa | 752 | 0.421 Pa
67 | 160876 | 100.0 CMH | 160 mmø | 1.4 m/s | 1.148 Pa | 947 | 0.201 Pa | 0.372 Pa
| 161239 | 100.0 CMH | 160 mmø | 1.4 m/s | 1.148 Pa | 115 | 0.024 Pa
| 162535 | 100.0 CMH | 160 mmø | 1.4 m/s | 1.148 Pa | 425 | 0.090 Pa
| 1734144 | 100.0 CMH | 160 mm | 1.4 m/s | 1.148 Pa | 269 | 0.057 Pa
68 | 190958 | 200.0 CMH | 200 mmx200 mm | 1.4 m/s | 1.160 Pa | 1500 | 0.243 Pa | 0.559 Pa
| 191140 | 200.0 CMH | 200 mmx200 mm | 1.4 m/s | 1.160 Pa | 965 | 0.156 Pa
| 191494 | 200.0 CMH | 200 mmx200 mm | 1.4 m/s | 1.160 Pa | 298 | 0.048 Pa
| 192472 | 200.0 CMH | 200 mmx200 mm | 1.4 m/s | 1.160 Pa | 161 | 0.026 Pa
| 194546 | 200.0 CMH | 200 mmx200 mm | 1.4 m/s | 1.160 Pa | 526 | 0.085 Pa
69 | 190228 | 300.0 CMH | 200 mmx200 mm | 2.1 m/s | 2.610 Pa | 1500 | 0.500 Pa | 1.151 Pa
| 191494 | 300.0 CMH | 200 mmx200 mm | 2.1 m/s | 2.610 Pa | 1202 | 0.401 Pa
| 193124 | 300.0 CMH | 200 mmx200 mm | 2.1 m/s | 2.610 Pa | 748 | 0.249 Pa
70 | 160099 | 150.0 CMH | 160 mmø | 2.1 m/s | 2.582 Pa | 926 | 0.404 Pa | 1.453 Pa
| 160375 | 150.0 CMH | 160 mmø | 2.1 m/s | 2.582 Pa | 146 | 0.064 Pa
| 160660 | 150.0 CMH | 160 mmø | 2.1 m/s | 2.582 Pa | 146 | 0.064 Pa
| 161701 | 150.0 CMH | 160 mmø | 2.1 m/s | 2.582 Pa | 776 | 0.339 Pa
| 161839 | 150.0 CMH | 160 mmø | 2.1 m/s | 2.582 Pa | 123 | 0.054 Pa
| 162574 | 150.0 CMH | 160 mmø | 2.1 m/s | 2.582 Pa | 587 | 0.256 Pa
| 162763 | 150.0 CMH | 160 mmø | 2.1 m/s | 2.582 Pa | 329 | 0.144 Pa
| 163132 | 150.0 CMH | 160 mmø | 2.1 m/s | 2.582 Pa | 294 | 0.129 Pa
71 | 160699 | 950.0 CMH | 280 mmø | 4.3 m/s | 11.044 Pa | 4075 | 3.277 Pa | 4.552 Pa
| 161212 | 950.0 CMH | 280 mmø | 4.3 m/s | 11.044 Pa | 43 | 0.035 Pa
| 161500 | 950.0 CMH | 280 mmø | 4.3 m/s | 11.044 Pa | 506 | 0.407 Pa
| 163270 | 950.0 CMH | 280 mmø | 4.3 m/s | 11.044 Pa | 901 | 0.725 Pa
| 1803672 | 950.0 CMH | 280 mmø | 4.3 m/s | 11.044 Pa | 135 | 0.109 Pa
72 | 161029 | 100.0 CMH | 160 mmø | 1.4 m/s | 1.148 Pa | 105 | 0.022 Pa | 0.393 Pa
| 162346 | 100.0 CMH | 160 mmø | 1.4 m/s | 1.148 Pa | 704 | 0.149 Pa
| 162886 | 100.0 CMH | 160 mmø | 1.4 m/s | 1.148 Pa | 259 | 0.055 Pa
| 1722952 | 100.0 CMH | 160 mm | 1.4 m/s | 1.148 Pa | 784 | 0.166 Pa
73 | 191996 | 100.0 CMH | 200 mmx200 mm | 0.7 m/s | 0.290 Pa | 46 | 0.002 Pa | 0.018 Pa
| 192472 | 100.0 CMH | 200 mmx200 mm | 0.7 m/s | 0.290 Pa | 339 | 0.016 Pa
74 | 173326 | 250.0 CMH | 250 mmø | 1.4 m/s | 1.203 Pa | 233 | 0.030 Pa | 0.446 Pa
| 173515 | 250.0 CMH | 250 mmø | 1.4 m/s | 1.203 Pa | 1233 | 0.156 Pa
| 174979 | 250.0 CMH | 250 mmø | 1.4 m/s | 1.203 Pa | 1179 | 0.149 Pa
| 175495 | 250.0 CMH | 250 mmø | 1.4 m/s | 1.203 Pa | 750 | 0.095 Pa
| 2305048 | 250.0 CMH | 250 mmø | 1.4 m/s | 1.203 Pa | 125 | 0.016 Pa
75 | 173239 | 150.0 CMH | 160 mmø | 2.1 m/s | 2.582 Pa | 124 | 0.054 Pa | 2.993 Pa
| 173968 | 150.0 CMH | 160 mmø | 2.1 m/s | 2.582 Pa | 48 | 0.021 Pa
| 174373 | 150.0 CMH | 160 mmø | 2.1 m/s | 2.582 Pa | 1000 | 0.437 Pa
| 174538 | 150.0 CMH | 160 mmø | 2.1 m/s | 2.582 Pa | 457 | 0.200 Pa
| 174640 | 150.0 CMH | 160 mmø | 2.1 m/s | 2.582 Pa | 5170 | 2.258 Pa
| 175186 | 150.0 CMH | 160 mmø | 2.1 m/s | 2.582 Pa | 53 | 0.023 Pa
76 | 159949 | 250.0 CMH | 250 mmø | 1.4 m/s | 1.203 Pa | 750 | 0.095 Pa | 0.449 Pa
| 160030 | 250.0 CMH | 250 mmø | 1.4 m/s | 1.203 Pa | 1056 | 0.134 Pa
| 163423 | 250.0 CMH | 250 mmø | 1.4 m/s | 1.203 Pa | 1590 | 0.201 Pa
| 2157420 | 250.0 CMH | 250 mmø | 1.4 m/s | 1.203 Pa | 154 | 0.020 Pa
77 | 160252 | 200.0 CMH | 160 mmø | 2.8 m/s | 4.591 Pa | 236 | 0.173 Pa | 0.483 Pa
| 161305 | 200.0 CMH | 160 mmø | 2.8 m/s | 4.591 Pa | 159 | 0.116 Pa
| 162154 | 200.0 CMH | 160 mmø | 2.8 m/s | 4.591 Pa | 265 | 0.194 Pa
78 | 160087 | 400.0 CMH | 180 mmø | 4.4 m/s | 11.464 Pa | 301 | 0.435 Pa | 18.823 Pa
| 160783 | 400.0 CMH | 180 mmø | 4.4 m/s | 11.464 Pa | 3286 | 4.750 Pa
| 160945 | 400.0 CMH | 180 mmø | 4.4 m/s | 11.464 Pa | 2408 | 3.481 Pa
| 161056 | 400.0 CMH | 180 mmø | 4.4 m/s | 11.464 Pa | 410 | 0.593 Pa
| 161194 | 400.0 CMH | 180 mmø | 4.4 m/s | 11.464 Pa | 550 | 0.796 Pa
| 162298 | 400.0 CMH | 180 mmø | 4.4 m/s | 11.464 Pa | 2539 | 3.669 Pa
| 162553 | 400.0 CMH | 180 mmø | 4.4 m/s | 11.464 Pa | 154 | 0.223 Pa
| 162595 | 400.0 CMH | 180 mmø | 4.4 m/s | 11.464 Pa | 532 | 0.769 Pa
| 162601 | 400.0 CMH | 180 mmø | 4.4 m/s | 11.464 Pa | 693 | 1.001 Pa
| 162913 | 400.0 CMH | 180 mmø | 4.4 m/s | 11.464 Pa | 514 | 0.743 Pa
| 1722166 | 400.0 CMH | 180 mmø | 4.4 m/s | 11.464 Pa | 1635 | 2.363 Pa
79 | 2291206 | 400.0 CMH | 250 mmø | 2.3 m/s | 3.081 Pa | 58 | 0.017 Pa | 0.017 Pa
80 | 161320 | 800.0 CMH | 250 mmø | 4.5 m/s | 12.323 Pa | 2485 | 2.545 Pa | 8.300 Pa
| 161815 | 800.0 CMH | 250 mmø | 4.5 m/s | 12.323 Pa | 3105 | 3.179 Pa
| 162253 | 800.0 CMH | 250 mmø | 4.5 m/s | 12.323 Pa | 220 | 0.225 Pa
| 162562 | 800.0 CMH | 250 mmø | 4.5 m/s | 12.323 Pa | 751 | 0.769 Pa
| 162613 | 800.0 CMH | 250 mmø | 4.5 m/s | 12.323 Pa | 1545 | 1.582 Pa
81 | 2290962 | 800.0 CMH | 280 mmø | 3.6 m/s | 7.832 Pa | 135 | 0.079 Pa | 0.079 Pa
82 | 160144 | 266.6 CMH | 250 mmø | 1.5 m/s | 1.369 Pa | 186 | 0.026 Pa | 0.066 Pa
| 163114 | 266.6 CMH | 250 mmø | 1.5 m/s | 1.369 Pa | 152 | 0.022 Pa
| 2291710 | 266.6 CMH | 250 mmø | 1.5 m/s | 1.369 Pa | 125 | 0.018 Pa
83 | 161092 | 799.8 CMH | 250 mmø | 4.5 m/s | 12.317 Pa | 258 | 0.264 Pa | 3.081 Pa
| 162580 | 799.8 CMH | 250 mmø | 4.5 m/s | 12.317 Pa | 501 | 0.513 Pa
| 162712 | 799.8 CMH | 250 mmø | 4.5 m/s | 12.317 Pa | 999 | 1.022 Pa
| 162718 | 799.8 CMH | 250 mmø | 4.5 m/s | 12.317 Pa | 786 | 0.805 Pa
| 2291721 | 799.8 CMH | 250 mmø | 4.5 m/s | 12.317 Pa | 467 | 0.478 Pa
84 | 162682 | 799.8 CMH | 200 mmø | 7.1 m/s | 30.072 Pa | 194 | 0.595 Pa | 0.595 Pa
86 | 191956 | 799.8 CMH | 300 mmx300 mm | 2.5 m/s | 3.664 Pa | 264 | 0.072 Pa | 0.072 Pa
87 | 156880 | 100.0 CMH | 160 mmø | 1.4 m/s | 1.148 Pa | 115 | 0.024 Pa | 0.400 Pa
| 156904 | 100.0 CMH | 160 mmø | 1.4 m/s | 1.148 Pa | 520 | 0.110 Pa
| 158830 | 100.0 CMH | 160 mmø | 1.4 m/s | 1.148 Pa | 994 | 0.211 Pa
| 461507 | 100.0 CMH | 160 mm | 1.4 m/s | 1.148 Pa | 260 | 0.055 Pa
88 | 173389 | 150.0 CMH | 160 mmø | 2.1 m/s | 2.582 Pa | 560 | 0.245 Pa | 0.556 Pa
| 173821 | 150.0 CMH | 160 mmø | 2.1 m/s | 2.582 Pa | 66 | 0.029 Pa
| 175588 | 150.0 CMH | 160 mmø | 2.1 m/s | 2.582 Pa | 205 | 0.089 Pa
| 175807 | 150.0 CMH | 160 mmø | 2.1 m/s | 2.582 Pa | 442 | 0.193 Pa
89 | 194214 | 949.8 CMH | 300 mmx300 mm | 2.9 m/s | 5.167 Pa | 715 | 0.265 Pa | 0.501 Pa
| 194236 | 949.8 CMH | 300 mmx300 mm | 2.9 m/s | 5.167 Pa | 636 | 0.236 Pa
90 | 190910 | 1449.8 CMH | 300 mmx300 mm | 4.5 m/s | 12.040 Pa | 63 | 0.050 Pa | 7.779 Pa
| 193508 | 1449.8 CMH | 300 mmx300 mm | 4.5 m/s | 12.040 Pa | 1438 | 1.147 Pa
| 194236 | 1449.8 CMH | 300 mmx300 mm | 4.5 m/s | 12.040 Pa | 864 | 0.690 Pa
| 194264 | 1449.8 CMH | 300 mmx300 mm | 4.5 m/s | 12.040 Pa | 1500 | 1.197 Pa
| 194850 | 1449.8 CMH | 300 mmx300 mm | 4.5 m/s | 12.040 Pa | 1500 | 1.197 Pa
| 195112 | 1449.8 CMH | 300 mmx300 mm | 4.5 m/s | 12.040 Pa | 1423 | 1.135 Pa
| 195146 | 1449.8 CMH | 300 mmx300 mm | 4.5 m/s | 12.040 Pa | 1382 | 1.103 Pa
| 195498 | 1449.8 CMH | 300 mmx300 mm | 4.5 m/s | 12.040 Pa | 1578 | 1.259 Pa
91 | 190542 | 1449.8 CMH | 300 mmx300 mm | 4.5 m/s | 12.040 Pa | 487 | 0.389 Pa | 3.310 Pa
| 191400 | 1449.8 CMH | 300 mmx300 mm | 4.5 m/s | 12.040 Pa | 487 | 0.388 Pa
| 194680 | 1449.8 CMH | 300 mmx300 mm | 4.5 m/s | 12.040 Pa | 361 | 0.288 Pa
| 194874 | 1449.8 CMH | 300 mmx300 mm | 4.5 m/s | 12.040 Pa | 1500 | 1.197 Pa
| 195610 | 1449.8 CMH | 300 mmx300 mm | 4.5 m/s | 12.040 Pa | 1313 | 1.048 Pa
92 | 194754 | 1449.8 CMH | 400 mmx400 mm | 2.5 m/s | 3.810 Pa | 276 | 0.054 Pa | 0.054 Pa
93 | 157153 | 100.0 CMH | 160 mmø | 1.4 m/s | 1.148 Pa | 115 | 0.024 Pa | 0.370 Pa
| 157291 | 100.0 CMH | 160 mmø | 1.4 m/s | 1.148 Pa | 425 | 0.090 Pa
| 157792 | 100.0 CMH | 160 mmø | 1.4 m/s | 1.148 Pa | 947 | 0.201 Pa
| 461464 | 100.0 CMH | 160 mm | 1.4 m/s | 1.148 Pa | 260 | 0.055 Pa
94 | 189876 | 200.0 CMH | 200 mmx200 mm | 1.4 m/s | 1.160 Pa | 526 | 0.085 Pa | 0.559 Pa
| 190078 | 200.0 CMH | 200 mmx200 mm | 1.4 m/s | 1.160 Pa | 965 | 0.156 Pa
| 190426 | 200.0 CMH | 200 mmx200 mm | 1.4 m/s | 1.160 Pa | 161 | 0.026 Pa
| 190466 | 200.0 CMH | 200 mmx200 mm | 1.4 m/s | 1.160 Pa | 1500 | 0.243 Pa
| 192068 | 200.0 CMH | 200 mmx200 mm | 1.4 m/s | 1.160 Pa | 298 | 0.048 Pa
95 | 189466 | 300.0 CMH | 200 mmx200 mm | 2.1 m/s | 2.610 Pa | 1500 | 0.500 Pa | 1.151 Pa
| 190246 | 300.0 CMH | 200 mmx200 mm | 2.1 m/s | 2.610 Pa | 748 | 0.249 Pa
| 192068 | 300.0 CMH | 200 mmx200 mm | 2.1 m/s | 2.610 Pa | 1202 | 0.401 Pa
96 | 157228 | 100.0 CMH | 160 mmø | 1.4 m/s | 1.148 Pa | 115 | 0.024 Pa | 0.390 Pa
| 158131 | 100.0 CMH | 160 mmø | 1.4 m/s | 1.148 Pa | 947 | 0.201 Pa
| 461478 | 100.0 CMH | 160 mm | 1.4 m/s | 1.148 Pa | 274 | 0.058 Pa
| 2174316 | 100.0 CMH | 160 mmø | 1.4 m/s | 1.148 Pa | 504 | 0.107 Pa
97 | 156814 | 150.0 CMH | 160 mmø | 2.1 m/s | 2.582 Pa | 179 | 0.078 Pa | 1.571 Pa
| 157687 | 150.0 CMH | 160 mmø | 2.1 m/s | 2.582 Pa | 162 | 0.071 Pa
| 157909 | 150.0 CMH | 160 mmø | 2.1 m/s | 2.582 Pa | 3018 | 1.318 Pa
| 1269099 | 150.0 CMH | 160 mmø | 2.1 m/s | 2.582 Pa | 237 | 0.103 Pa
98 | 159589 | 150.0 CMH | 160 mmø | 2.1 m/s | 2.582 Pa | 86 | 0.038 Pa | 0.119 Pa
| 461561 | 150.0 CMH | 160 mmø | 2.1 m/s | 2.582 Pa | 50 | 0.022 Pa
| 2173890 | 150.0 CMH | 160 mmø | 2.1 m/s | 2.582 Pa | 137 | 0.060 Pa
99 | 162793 | 250.0 CMH | 250 mmø | 1.4 m/s | 1.203 Pa | 1000 | 0.127 Pa | 0.227 Pa
| 1784753 | 250.0 CMH | 250 mm | 1.4 m/s | 1.203 Pa | 797 | 0.101 Pa
100 | 159970 | 500.0 CMH | 250 mmø | 2.8 m/s | 4.814 Pa | 3277 | 1.433 Pa | 2.346 Pa
| 160639 | 500.0 CMH | 250 mmø | 2.8 m/s | 4.814 Pa | 427 | 0.187 Pa
| 160732 | 500.0 CMH | 250 mmø | 2.8 m/s | 4.814 Pa | 1662 | 0.727 Pa
101 | 176200 | 266.6 CMH | 250 mmø | 1.5 m/s | 1.369 Pa | 114 | 0.016 Pa | 0.076 Pa
| 2647347 | 266.6 CMH | 250 mm | 1.5 m/s | 1.369 Pa | 425 | 0.060 Pa
102 | 173470 | 799.8 CMH | 250 mmø | 4.5 m/s | 12.317 Pa | 1788 | 1.830 Pa | 3.812 Pa
| 174394 | 799.8 CMH | 250 mmø | 4.5 m/s | 12.317 Pa | 562 | 0.575 Pa
| 175600 | 799.8 CMH | 250 mmø | 4.5 m/s | 12.317 Pa | 1000 | 1.023 Pa
| 175954 | 799.8 CMH | 250 mmø | 4.5 m/s | 12.317 Pa | 375 | 0.384 Pa
104 | 173302 | 799.8 CMH | 250 mmø | 4.5 m/s | 12.317 Pa | 137 | 0.140 Pa | 0.573 Pa
| 173743 | 799.8 CMH | 250 mmø | 4.5 m/s | 12.317 Pa | 207 | 0.212 Pa
| 174160 | 799.8 CMH | 250 mmø | 4.5 m/s | 12.317 Pa | 81 | 0.083 Pa
| 1562659 | 799.8 CMH | 250 mmø | 4.5 m/s | 12.317 Pa | 135 | 0.138 Pa
105 | 194214 | 799.8 CMH | 300 mmx300 mm | 0.0 m/s | 0.000 Pa | 715 | 0.000 Pa | 0.000 Pa
106 | 173917 | 100.0 CMH | 160 mmø | 1.4 m/s | 1.148 Pa | 457 | 0.097 Pa | 0.389 Pa
| 174460 | 100.0 CMH | 160 mmø | 1.4 m/s | 1.148 Pa | 105 | 0.022 Pa
| 175906 | 100.0 CMH | 160 mmø | 1.4 m/s | 1.148 Pa | 247 | 0.052 Pa
| 176185 | 100.0 CMH | 160 mmø | 1.4 m/s | 1.148 Pa | 260 | 0.055 Pa
| 1607367 | 100.0 CMH | 160 mm | 1.4 m/s | 1.148 Pa | 767 | 0.163 Pa
107 | 189950 | 100.0 CMH | 200 mmx200 mm | 0.7 m/s | 0.290 Pa | 339 | 0.016 Pa | 0.018 Pa
| 191634 | 100.0 CMH | 200 mmx200 mm | 0.7 m/s | 0.290 Pa | 46 | 0.002 Pa
108 | 189950 | 200.0 CMH | 200 mmx200 mm | 1.4 m/s | 1.160 Pa | 161 | 0.026 Pa | 0.559 Pa
| 190340 | 200.0 CMH | 200 mmx200 mm | 1.4 m/s | 1.160 Pa | 298 | 0.048 Pa
| 191394 | 200.0 CMH | 200 mmx200 mm | 1.4 m/s | 1.160 Pa | 526 | 0.085 Pa
| 194094 | 200.0 CMH | 200 mmx200 mm | 1.4 m/s | 1.160 Pa | 965 | 0.156 Pa
| 194232 | 200.0 CMH | 200 mmx200 mm | 1.4 m/s | 1.160 Pa | 1500 | 0.243 Pa
109 | 190340 | 300.0 CMH | 200 mmx200 mm | 2.1 m/s | 2.610 Pa | 1202 | 0.401 Pa | 1.151 Pa
| 194980 | 300.0 CMH | 200 mmx200 mm | 2.1 m/s | 2.610 Pa | 748 | 0.249 Pa
| 194994 | 300.0 CMH | 200 mmx200 mm | 2.1 m/s | 2.610 Pa | 1500 | 0.500 Pa
110 | 190976 | 400.0 CMH | 200 mmx200 mm | 2.8 m/s | 4.640 Pa | 1151 | 0.643 Pa | 1.902 Pa
| 191034 | 400.0 CMH | 200 mmx200 mm | 2.8 m/s | 4.640 Pa | 1500 | 0.838 Pa
| 194980 | 400.0 CMH | 200 mmx200 mm | 2.8 m/s | 4.640 Pa | 752 | 0.421 Pa
111 | 190976 | 500.0 CMH | 200 mmx200 mm | 3.5 m/s | 7.250 Pa | 179 | 0.150 Pa | 0.503 Pa
| 191044 | 500.0 CMH | 200 mmx200 mm | 3.5 m/s | 7.250 Pa | 422 | 0.353 Pa
112 | 192114 | 500.0 CMH | 200 mmx200 mm | 3.5 m/s | 7.250 Pa | 1144 | 0.957 Pa | 1.629 Pa
| 194936 | 500.0 CMH | 200 mmx200 mm | 3.5 m/s | 7.250 Pa | 804 | 0.672 Pa
114 | 192688 | 500.0 CMH | 200 mmx200 mm | 3.5 m/s | 7.250 Pa | 293 | 0.245 Pa | 1.508 Pa
| 194226 | 500.0 CMH | 200 mmx200 mm | 3.5 m/s | 7.250 Pa | 50 | 0.042 Pa
| 195018 | 500.0 CMH | 200 mmx200 mm | 3.5 m/s | 7.250 Pa | 1057 | 0.883 Pa
| 195428 | 500.0 CMH | 200 mmx200 mm | 3.5 m/s | 7.250 Pa | 404 | 0.338 Pa
115 | 160309 | 250.0 CMH | 250 mmø | 1.4 m/s | 1.203 Pa | 608 | 0.077 Pa | 1.110 Pa
| 160489 | 250.0 CMH | 250 mmø | 1.4 m/s | 1.203 Pa | 182 | 0.023 Pa
| 161497 | 250.0 CMH | 250 mmø | 1.4 m/s | 1.203 Pa | 133 | 0.017 Pa
| 162289 | 250.0 CMH | 250 mmø | 1.4 m/s | 1.203 Pa | 2500 | 0.316 Pa
| 162328 | 250.0 CMH | 250 mmø | 1.4 m/s | 1.203 Pa | 697 | 0.088 Pa
| 162433 | 250.0 CMH | 250 mmø | 1.4 m/s | 1.203 Pa | 869 | 0.110 Pa
| 162865 | 250.0 CMH | 250 mmø | 1.4 m/s | 1.203 Pa | 2124 | 0.269 Pa
| 163024 | 250.0 CMH | 250 mmø | 1.4 m/s | 1.203 Pa | 342 | 0.043 Pa
| 1722373 | 250.0 CMH | 250 mmø | 1.4 m/s | 1.203 Pa | 202 | 0.026 Pa
| 1722391 | 250.0 CMH | 250 mmø | 1.4 m/s | 1.203 Pa | 562 | 0.071 Pa
| 2291395 | 250.0 CMH | 250 mmø | 1.4 m/s | 1.203 Pa | 554 | 0.070 Pa
116 | 159997 | 400.0 CMH | 250 mmø | 2.3 m/s | 3.081 Pa | 1648 | 0.482 Pa | 1.845 Pa
| 160366 | 400.0 CMH | 250 mmø | 2.3 m/s | 3.081 Pa | 186 | 0.055 Pa
| 161533 | 400.0 CMH | 250 mmø | 2.3 m/s | 3.081 Pa | 606 | 0.177 Pa
| 161650 | 400.0 CMH | 250 mmø | 2.3 m/s | 3.081 Pa | 3707 | 1.086 Pa
| 2157845 | 400.0 CMH | 250 mmø | 2.3 m/s | 3.081 Pa | 154 | 0.045 Pa
117 | 160771 | 200.0 CMH | 160 mmø | 2.8 m/s | 4.591 Pa | 264 | 0.193 Pa | 3.486 Pa
| 160780 | 200.0 CMH | 160 mmø | 2.8 m/s | 4.591 Pa | 4123 | 3.017 Pa
| 160900 | 200.0 CMH | 160 mmø | 2.8 m/s | 4.591 Pa | 236 | 0.173 Pa
| 163030 | 200.0 CMH | 160 mmø | 2.8 m/s | 4.591 Pa | 140 | 0.102 Pa
119 | 162193 | 150.0 CMH | 160 mmø | 2.1 m/s | 2.582 Pa | 53 | 0.023 Pa | 3.143 Pa
| 162997 | 150.0 CMH | 160 mmø | 2.1 m/s | 2.582 Pa | 457 | 0.200 Pa
| 163381 | 150.0 CMH | 160 mmø | 2.1 m/s | 2.582 Pa | 6687 | 2.921 Pa
120 | 160381 | 150.0 CMH | 160 mmø | 2.1 m/s | 2.582 Pa | 93 | 0.041 Pa | 0.317 Pa
| 161410 | 150.0 CMH | 160 mmø | 2.1 m/s | 2.582 Pa | 195 | 0.085 Pa
| 161419 | 150.0 CMH | 160 mmø | 2.1 m/s | 2.582 Pa | 21 | 0.009 Pa
| 161953 | 150.0 CMH | 160 mmø | 2.1 m/s | 2.582 Pa | 109 | 0.048 Pa
| 2159678 | 150.0 CMH | 160 mmø | 2.1 m/s | 2.582 Pa | 129 | 0.056 Pa
| 2159685 | 150.0 CMH | 160 mmø | 2.1 m/s | 2.582 Pa | 178 | 0.078 Pa
121 | 161893 | 150.0 CMH | 160 mmø | 2.1 m/s | 2.582 Pa | 21 | 0.009 Pa | 0.242 Pa
| 162322 | 150.0 CMH | 160 mmø | 2.1 m/s | 2.582 Pa | 175 | 0.076 Pa
| 162352 | 150.0 CMH | 160 mmø | 2.1 m/s | 2.582 Pa | 27 | 0.012 Pa
| 162484 | 150.0 CMH | 160 mmø | 2.1 m/s | 2.582 Pa | 70 | 0.031 Pa
| 163042 | 150.0 CMH | 160 mmø | 2.1 m/s | 2.582 Pa | 163 | 0.071 Pa
| 163225 | 150.0 CMH | 160 mmø | 2.1 m/s | 2.582 Pa | 98 | 0.043 Pa
122 | 161077 | 266.6 CMH | 250 mmø | 1.5 m/s | 1.369 Pa | 54 | 0.008 Pa | 0.896 Pa
| 162295 | 266.6 CMH | 250 mmø | 1.5 m/s | 1.369 Pa | 183 | 0.026 Pa
| 162406 | 266.6 CMH | 250 mmø | 1.5 m/s | 1.369 Pa | 150 | 0.021 Pa
| 2289589 | 266.6 CMH | 250 mmø | 1.5 m/s | 1.369 Pa | 5930 | 0.841 Pa
123 | 2292089 | 533.2 CMH | 250 mmø | 3.0 m/s | 5.474 Pa | 5926 | 2.909 Pa | 2.909 Pa
124 | 1784937 | 100.0 CMH | 160 mmø | 1.4 m/s | 1.148 Pa | 261 | 0.055 Pa | 0.102 Pa
| 1784941 | 100.0 CMH | 160 mmø | 1.4 m/s | 1.148 Pa | 20 | 0.004 Pa
| 1784943 | 100.0 CMH | 160 mmø | 1.4 m/s | 1.148 Pa | 176 | 0.037 Pa
| 1784945 | 100.0 CMH | 160 mmø | 1.4 m/s | 1.148 Pa | 27 | 0.006 Pa
125 | 160831 | 100.0 CMH | 160 mmø | 1.4 m/s | 1.148 Pa | 115 | 0.024 Pa | 0.372 Pa
| 161173 | 100.0 CMH | 160 mmø | 1.4 m/s | 1.148 Pa | 947 | 0.201 Pa
| 162418 | 100.0 CMH | 160 mmø | 1.4 m/s | 1.148 Pa | 425 | 0.090 Pa
| 1734190 | 100.0 CMH | 160 mm | 1.4 m/s | 1.148 Pa | 269 | 0.057 Pa
126 | 1784883 | 150.0 CMH | 160 mmø | 2.1 m/s | 2.582 Pa | 163 | 0.071 Pa | 0.251 Pa
| 1784887 | 150.0 CMH | 160 mmø | 2.1 m/s | 2.582 Pa | 20 | 0.009 Pa
| 1784889 | 150.0 CMH | 160 mmø | 2.1 m/s | 2.582 Pa | 176 | 0.077 Pa
| 1784891 | 150.0 CMH | 160 mmø | 2.1 m/s | 2.582 Pa | 27 | 0.012 Pa
| 2289975 | 150.0 CMH | 160 mmø | 2.1 m/s | 2.582 Pa | 95 | 0.041 Pa
| 2290809 | 150.0 CMH | 160 mmø | 2.1 m/s | 2.582 Pa | 95 | 0.041 Pa
127 | 161962 | 250.0 CMH | 250 mmø | 1.4 m/s | 1.203 Pa | 1000 | 0.127 Pa | 0.228 Pa
| 1784751 | 250.0 CMH | 250 mm | 1.4 m/s | 1.203 Pa | 802 | 0.102 Pa
128 | 2647362 | 266.6 CMH | 250 mm | 1.5 m/s | 1.369 Pa | 535 | 0.076 Pa | 0.076 Pa
129 | 175267 | 533.2 CMH | 250 mmø | 3.0 m/s | 5.474 Pa | 644 | 0.316 Pa | 2.901 Pa
| 176248 | 533.2 CMH | 250 mmø | 3.0 m/s | 5.474 Pa | 5267 | 2.585 Pa
130 | 175552 | 266.6 CMH | 250 mmø | 1.5 m/s | 1.369 Pa | 714 | 0.101 Pa | 0.840 Pa
| 175987 | 266.6 CMH | 250 mmø | 1.5 m/s | 1.369 Pa | 5207 | 0.739 Pa
131 | 159931 | 400.0 CMH | 250 mmø | 2.3 m/s | 3.081 Pa | 390 | 0.114 Pa | 1.040 Pa
| 160078 | 400.0 CMH | 250 mmø | 2.3 m/s | 3.081 Pa | 86 | 0.025 Pa
| 160393 | 400.0 CMH | 250 mmø | 2.3 m/s | 3.081 Pa | 331 | 0.097 Pa
| 161185 | 400.0 CMH | 250 mmø | 2.3 m/s | 3.081 Pa | 171 | 0.050 Pa
| 161245 | 400.0 CMH | 250 mmø | 2.3 m/s | 3.081 Pa | 469 | 0.137 Pa
| 161506 | 400.0 CMH | 250 mmø | 2.3 m/s | 3.081 Pa | 500 | 0.146 Pa
| 161785 | 400.0 CMH | 250 mmø | 2.3 m/s | 3.081 Pa | 651 | 0.191 Pa
| 162451 | 400.0 CMH | 250 mmø | 2.3 m/s | 3.081 Pa | 678 | 0.199 Pa
| 1722152 | 400.0 CMH | 250 mmø | 2.3 m/s | 3.081 Pa | 276 | 0.081 Pa
132 | 159925 | 266.6 CMH | 250 mmø | 1.5 m/s | 1.369 Pa | 149 | 0.021 Pa | 0.063 Pa
| 160753 | 266.6 CMH | 250 mmø | 1.5 m/s | 1.369 Pa | 114 | 0.016 Pa
| 162220 | 266.6 CMH | 250 mmø | 1.5 m/s | 1.369 Pa | 183 | 0.026 Pa
133 | 172849 | 125.0 CMH | 160 mmø | 1.7 m/s | 1.793 Pa | 177 | 0.056 Pa | 0.080 Pa
| 174202 | 125.0 CMH | 160 mmø | 1.7 m/s | 1.793 Pa | 75 | 0.024 Pa
134 | 173677 | 250.0 CMH | 160 mmø | 3.5 m/s | 7.173 Pa | 198 | 0.217 Pa | 5.037 Pa
| 173902 | 250.0 CMH | 160 mmø | 3.5 m/s | 7.173 Pa | 421 | 0.460 Pa
| 174397 | 250.0 CMH | 160 mmø | 3.5 m/s | 7.173 Pa | 912 | 0.999 Pa
| 1836065 | 250.0 CMH | 160 mmø | 3.5 m/s | 7.173 Pa | 3070 | 3.360 Pa
136 | 175702 | 350.0 CMH | 250 mmø | 2.0 m/s | 2.359 Pa | 3191 | 0.736 Pa | 0.736 Pa
137 | 173503 | 500.0 CMH | 250 mmø | 2.8 m/s | 4.814 Pa | 3190 | 1.395 Pa | 1.395 Pa
138 | 173941 | 600.0 CMH | 250 mmø | 3.4 m/s | 6.932 Pa | 3190 | 1.938 Pa | 1.938 Pa
139 | 175639 | 750.0 CMH | 250 mmø | 4.2 m/s | 10.831 Pa | 209 | 0.190 Pa | 0.190 Pa
141 | 173170 | 900.0 CMH | 280 mmø | 4.1 m/s | 9.912 Pa | 828 | 0.604 Pa | 3.907 Pa
| 174124 | 900.0 CMH | 280 mmø | 4.1 m/s | 9.912 Pa | 1710 | 1.247 Pa
| 174514 | 900.0 CMH | 280 mmø | 4.1 m/s | 9.912 Pa | 2175 | 1.585 Pa
| 175558 | 900.0 CMH | 280 mmø | 4.1 m/s | 9.912 Pa | 357 | 0.260 Pa
| 175720 | 900.0 CMH | 280 mmø | 4.1 m/s | 9.912 Pa | 290 | 0.211 Pa
142 | 195150 | 900.0 CMH | 400 mmx400 mm | 1.6 m/s | 1.468 Pa | 129 | 0.011 Pa | 0.029 Pa
| 1744339 | 900.0 CMH | 400 mmx400 mm | 1.6 m/s | 1.468 Pa | 211 | 0.018 Pa
143 | 190832 | 2100.0 CMH | 400 mmx400 mm | 3.6 m/s | 7.993 Pa | 27 | 0.010 Pa | 1.426 Pa
| 1744339 | 2100.0 CMH | 400 mmx400 mm | 3.6 m/s | 7.993 Pa | 212 | 0.081 Pa
| 1836006 | 2100.0 CMH | 400 mmx400 mm | 3.6 m/s | 7.993 Pa | 1500 | 0.576 Pa
| 1836007 | 2100.0 CMH | 400 mmx400 mm | 3.6 m/s | 7.993 Pa | 792 | 0.304 Pa
| 1836032 | 2100.0 CMH | 400 mmx400 mm | 3.6 m/s | 7.993 Pa | 1098 | 0.421 Pa
| 1836033 | 2100.0 CMH | 400 mmx400 mm | 3.6 m/s | 7.993 Pa | 84 | 0.032 Pa
144 | 1835990 | 2100.0 CMH | 450 mmx450 mm | 2.9 m/s | 4.990 Pa | 1172 | 0.254 Pa | 0.254 Pa
145 | 190692 | 2350.0 CMH | 450 mmx450 mm | 3.2 m/s | 6.249 Pa | 799 | 0.212 Pa | 0.279 Pa
| 1835990 | 2350.0 CMH | 450 mmx450 mm | 3.2 m/s | 6.249 Pa | 252 | 0.067 Pa
146 | 193868 | 4750.0 CMH | 600 mmx600 mm | 3.7 m/s | 8.077 Pa | 629 | 0.149 Pa | 0.692 Pa
| 195550 | 4750.0 CMH | 600 mmx600 mm | 3.7 m/s | 8.077 Pa | 800 | 0.189 Pa
| 195588 | 4750.0 CMH | 600 mmx600 mm | 3.7 m/s | 8.077 Pa | 1500 | 0.354 Pa
147 | 194954 | 4750.0 CMH | 700 mmx700 mm | 2.7 m/s | 4.360 Pa | 855 | 0.095 Pa | 0.095 Pa
148 | 173260 | 175.0 CMH | 160 mmø | 2.4 m/s | 3.515 Pa | 397 | 0.229 Pa | 2.862 Pa
| 175459 | 175.0 CMH | 160 mmø | 2.4 m/s | 3.515 Pa | 4180 | 2.406 Pa
| 175771 | 175.0 CMH | 160 mmø | 2.4 m/s | 3.515 Pa | 393 | 0.226 Pa
149 | 173563 | 350.0 CMH | 160 mmø | 4.8 m/s | 14.059 Pa | 2773 | 5.593 Pa | 15.078 Pa
| 173638 | 350.0 CMH | 160 mmø | 4.8 m/s | 14.059 Pa | 3430 | 6.919 Pa
| 174763 | 350.0 CMH | 160 mmø | 4.8 m/s | 14.059 Pa | 195 | 0.393 Pa
| 176209 | 350.0 CMH | 160 mmø | 4.8 m/s | 14.059 Pa | 357 | 0.720 Pa
| 1749137 | 350.0 CMH | 160 mmø | 4.8 m/s | 14.059 Pa | 11 | 0.021 Pa
| 2479826 | 350.0 CMH | 160 mmø | 4.8 m/s | 14.059 Pa | 709 | 1.430 Pa
151 | 173782 | 950.0 CMH | 280 mmø | 4.3 m/s | 11.044 Pa | 62 | 0.049 Pa | 10.303 Pa
| 174883 | 950.0 CMH | 280 mmø | 4.3 m/s | 11.044 Pa | 231 | 0.186 Pa
| 175354 | 950.0 CMH | 280 mmø | 4.3 m/s | 11.044 Pa | 2767 | 2.225 Pa
| 175396 | 950.0 CMH | 280 mmø | 4.3 m/s | 11.044 Pa | 2413 | 1.940 Pa
| 175438 | 950.0 CMH | 280 mmø | 4.3 m/s | 11.044 Pa | 132 | 0.106 Pa
| 175642 | 950.0 CMH | 280 mmø | 4.3 m/s | 11.044 Pa | 146 | 0.118 Pa
| 175654 | 950.0 CMH | 280 mmø | 4.3 m/s | 11.044 Pa | 3783 | 3.043 Pa
| 175675 | 950.0 CMH | 280 mmø | 4.3 m/s | 11.044 Pa | 187 | 0.151 Pa
| 175969 | 950.0 CMH | 280 mmø | 4.3 m/s | 11.044 Pa | 77 | 0.062 Pa
| 175993 | 950.0 CMH | 280 mmø | 4.3 m/s | 11.044 Pa | 513 | 0.413 Pa
| 176188 | 950.0 CMH | 280 mmø | 4.3 m/s | 11.044 Pa | 2499 | 2.010 Pa
152 | 173122 | 1075.0 CMH | 280 mmø | 4.8 m/s | 14.142 Pa | 270 | 0.272 Pa | 5.851 Pa
| 173827 | 1075.0 CMH | 280 mmø | 4.8 m/s | 14.142 Pa | 520 | 0.523 Pa
| 175333 | 1075.0 CMH | 280 mmø | 4.8 m/s | 14.142 Pa | 347 | 0.350 Pa
| 176305 | 1075.0 CMH | 280 mmø | 4.8 m/s | 14.142 Pa | 4671 | 4.705 Pa
153 | 173386 | 1200.0 CMH | 280 mmø | 5.4 m/s | 17.622 Pa | 5224 | 6.436 Pa | 11.521 Pa
| 174070 | 1200.0 CMH | 280 mmø | 5.4 m/s | 17.622 Pa | 711 | 0.876 Pa
| 174835 | 1200.0 CMH | 280 mmø | 5.4 m/s | 17.622 Pa | 586 | 0.722 Pa
| 175144 | 1200.0 CMH | 280 mmø | 5.4 m/s | 17.622 Pa | 1529 | 1.883 Pa
| 175756 | 1200.0 CMH | 280 mmø | 5.4 m/s | 17.622 Pa | 1147 | 1.413 Pa
| 2173264 | 1200.0 CMH | 280 mmø | 5.4 m/s | 17.622 Pa | 155 | 0.191 Pa
154 | 2640809 | 300.0 CMH | 200 mm | 2.7 m/s | 4.231 Pa | 486 | 0.250 Pa | 0.250 Pa
156 | 174655 | 600.0 CMH | 250 mmø | 3.4 m/s | 6.932 Pa | 1463 | 0.889 Pa | 1.204 Pa
| 176236 | 600.0 CMH | 250 mmø | 3.4 m/s | 6.932 Pa | 518 | 0.315 Pa
157 | 158638 | 125.0 CMH | 160 mmø | 1.7 m/s | 1.793 Pa | 19 | 0.006 Pa | 0.979 Pa
| 158872 | 125.0 CMH | 160 mmø | 1.7 m/s | 1.793 Pa | 2947 | 0.930 Pa
| 159049 | 125.0 CMH | 160 mmø | 1.7 m/s | 1.793 Pa | 137 | 0.043 Pa
158 | 156925 | 250.0 CMH | 160 mmø | 3.5 m/s | 7.173 Pa | 182 | 0.199 Pa | 0.593 Pa
| 157045 | 250.0 CMH | 160 mmø | 3.5 m/s | 7.173 Pa | 282 | 0.308 Pa
| 158284 | 250.0 CMH | 160 mmø | 3.5 m/s | 7.173 Pa | 78 | 0.086 Pa
159 | 156565 | 850.0 CMH | 280 mmø | 3.8 m/s | 8.841 Pa | 110 | 0.072 Pa | 2.346 Pa
| 156958 | 850.0 CMH | 280 mmø | 3.8 m/s | 8.841 Pa | 145 | 0.095 Pa
| 157723 | 850.0 CMH | 280 mmø | 3.8 m/s | 8.841 Pa | 128 | 0.084 Pa
| 158341 | 850.0 CMH | 280 mmø | 3.8 m/s | 8.841 Pa | 1304 | 0.857 Pa
| 158833 | 850.0 CMH | 280 mmø | 3.8 m/s | 8.841 Pa | 1698 | 1.116 Pa
| 159436 | 850.0 CMH | 280 mmø | 3.8 m/s | 8.841 Pa | 62 | 0.041 Pa
| 159745 | 850.0 CMH | 280 mmø | 3.8 m/s | 8.841 Pa | 122 | 0.080 Pa
160 | 192712 | 850.0 CMH | 400 mmx300 mm | 2.0 m/s | 2.328 Pa | 246 | 0.038 Pa | 0.038 Pa
161 | 189866 | 2400.0 CMH | 400 mmx300 mm | 5.6 m/s | 18.559 Pa | 1006 | 1.009 Pa | 3.305 Pa
| 190356 | 2400.0 CMH | 400 mmx300 mm | 5.6 m/s | 18.559 Pa | 558 | 0.560 Pa
| 190644 | 2400.0 CMH | 400 mmx300 mm | 5.6 m/s | 18.559 Pa | 410 | 0.411 Pa
| 192712 | 2400.0 CMH | 400 mmx300 mm | 5.6 m/s | 18.559 Pa | 246 | 0.247 Pa
| 193976 | 2400.0 CMH | 400 mmx300 mm | 5.6 m/s | 18.559 Pa | 75 | 0.075 Pa
| 194528 | 2400.0 CMH | 400 mmx300 mm | 5.6 m/s | 18.559 Pa | 1000 | 1.003 Pa
163 | 190660 | 2400.0 CMH | 400 mmx300 mm | 5.6 m/s | 18.559 Pa | 100 | 0.100 Pa | 0.100 Pa
164 | 189444 | 2400.0 CMH | 400 mmx400 mm | 4.2 m/s | 10.439 Pa | 912 | 0.446 Pa | 2.164 Pa
| 190332 | 2400.0 CMH | 400 mmx400 mm | 4.2 m/s | 10.439 Pa | 800 | 0.391 Pa
| 190982 | 2400.0 CMH | 400 mmx400 mm | 4.2 m/s | 10.439 Pa | 233 | 0.114 Pa
| 191228 | 2400.0 CMH | 400 mmx400 mm | 4.2 m/s | 10.439 Pa | 1500 | 0.734 Pa
| 192356 | 2400.0 CMH | 400 mmx400 mm | 4.2 m/s | 10.439 Pa | 979 | 0.479 Pa
165 | 189888 | 2400.0 CMH | 600 mmx600 mm | 1.9 m/s | 2.062 Pa | 700 | 0.048 Pa | 0.060 Pa
| 193868 | 2400.0 CMH | 600 mmx600 mm | 1.9 m/s | 2.062 Pa | 171 | 0.012 Pa
166 | 173527 | 150.0 CMH | 160 mmø | 2.1 m/s | 2.582 Pa | 27 | 0.012 Pa | 0.171 Pa
| 174256 | 150.0 CMH | 160 mmø | 2.1 m/s | 2.582 Pa | 160 | 0.070 Pa
| 175444 | 150.0 CMH | 160 mmø | 2.1 m/s | 2.582 Pa | 42 | 0.018 Pa
| 175879 | 150.0 CMH | 160 mmø | 2.1 m/s | 2.582 Pa | 163 | 0.071 Pa
167 | 173293 | 100.0 CMH | 160 mmø | 1.4 m/s | 1.148 Pa | 42 | 0.009 Pa | 0.104 Pa
| 173464 | 100.0 CMH | 160 mmø | 1.4 m/s | 1.148 Pa | 163 | 0.035 Pa
| 174475 | 100.0 CMH | 160 mmø | 1.4 m/s | 1.148 Pa | 160 | 0.034 Pa
| 174490 | 100.0 CMH | 160 mmø | 1.4 m/s | 1.148 Pa | 30 | 0.006 Pa
| 175666 | 100.0 CMH | 160 mmø | 1.4 m/s | 1.148 Pa | 98 | 0.021 Pa
168 | 173767 | 150.0 CMH | 160 mmø | 2.1 m/s | 2.582 Pa | 42 | 0.018 Pa | 0.215 Pa
| 174061 | 150.0 CMH | 160 mmø | 2.1 m/s | 2.582 Pa | 160 | 0.070 Pa
| 174946 | 150.0 CMH | 160 mmø | 2.1 m/s | 2.582 Pa | 98 | 0.043 Pa
| 175912 | 150.0 CMH | 160 mmø | 2.1 m/s | 2.582 Pa | 30 | 0.013 Pa
| 175972 | 150.0 CMH | 160 mmø | 2.1 m/s | 2.582 Pa | 163 | 0.071 Pa
169 | 172867 | 250.0 CMH | 200 mmø | 2.2 m/s | 2.938 Pa | 472 | 0.175 Pa | 1.605 Pa
| 173365 | 250.0 CMH | 200 mmø | 2.2 m/s | 2.938 Pa | 84 | 0.031 Pa
| 174493 | 250.0 CMH | 200 mmø | 2.2 m/s | 2.938 Pa | 50 | 0.019 Pa
| 174769 | 250.0 CMH | 200 mmø | 2.2 m/s | 2.938 Pa | 426 | 0.158 Pa
| 175246 | 250.0 CMH | 200 mmø | 2.2 m/s | 2.938 Pa | 4 | 0.001 Pa
| 175381 | 250.0 CMH | 200 mmø | 2.2 m/s | 2.938 Pa | 2231 | 0.828 Pa
| 175831 | 250.0 CMH | 200 mmø | 2.2 m/s | 2.938 Pa | 50 | 0.019 Pa
| 175903 | 250.0 CMH | 200 mmø | 2.2 m/s | 2.938 Pa | 251 | 0.093 Pa
| 175927 | 250.0 CMH | 200 mmø | 2.2 m/s | 2.938 Pa | 400 | 0.148 Pa
| 175957 | 250.0 CMH | 200 mmø | 2.2 m/s | 2.938 Pa | 358 | 0.133 Pa
170 | 173998 | 175.0 CMH | 160 mmø | 2.4 m/s | 3.515 Pa | 417 | 0.240 Pa | 0.522 Pa
| 2647456 | 175.0 CMH | 160 mm | 2.4 m/s | 3.515 Pa | 489 | 0.282 Pa
171 | 157831 | 125.0 CMH | 160 mmø | 1.7 m/s | 1.793 Pa | 19 | 0.006 Pa | 0.059 Pa
| 159673 | 125.0 CMH | 160 mmø | 1.7 m/s | 1.793 Pa | 167 | 0.053 Pa
172 | 160291 | 250.0 CMH | 200 mmø | 2.2 m/s | 2.938 Pa | 1748 | 0.648 Pa | 1.609 Pa
| 161371 | 250.0 CMH | 200 mmø | 2.2 m/s | 2.938 Pa | 45 | 0.017 Pa
| 162091 | 250.0 CMH | 200 mmø | 2.2 m/s | 2.938 Pa | 1406 | 0.522 Pa
| 162367 | 250.0 CMH | 200 mmø | 2.2 m/s | 2.938 Pa | 153 | 0.057 Pa
| 162472 | 250.0 CMH | 200 mmø | 2.2 m/s | 2.938 Pa | 618 | 0.229 Pa
| 163141 | 250.0 CMH | 200 mmø | 2.2 m/s | 2.938 Pa | 251 | 0.093 Pa
| 2159230 | 250.0 CMH | 200 mmø | 2.2 m/s | 2.938 Pa | 117 | 0.044 Pa
173 | 156817 | 100.0 CMH | 160 mmø | 1.4 m/s | 1.148 Pa | 854 | 0.181 Pa | 0.272 Pa
| 156889 | 100.0 CMH | 160 mmø | 1.4 m/s | 1.148 Pa | 193 | 0.041 Pa
| 157540 | 100.0 CMH | 160 mmø | 1.4 m/s | 1.148 Pa | 19 | 0.004 Pa
| 157819 | 100.0 CMH | 160 mmø | 1.4 m/s | 1.148 Pa | 137 | 0.029 Pa
| 159700 | 100.0 CMH | 160 mmø | 1.4 m/s | 1.148 Pa | 82 | 0.017 Pa
174 | 157312 | 600.0 CMH | 250 mmø | 3.4 m/s | 6.932 Pa | 1087 | 0.661 Pa | 3.394 Pa
| 158842 | 600.0 CMH | 250 mmø | 3.4 m/s | 6.932 Pa | 4500 | 2.734 Pa
176 | 172939 | 150.0 CMH | 160 mmø | 2.1 m/s | 2.582 Pa | 109 | 0.048 Pa | 0.210 Pa
| 173617 | 150.0 CMH | 160 mmø | 2.1 m/s | 2.582 Pa | 60 | 0.026 Pa
| 175324 | 150.0 CMH | 160 mmø | 2.1 m/s | 2.582 Pa | 180 | 0.079 Pa
| 176020 | 150.0 CMH | 160 mmø | 2.1 m/s | 2.582 Pa | 90 | 0.039 Pa
| 176086 | 150.0 CMH | 160 mmø | 2.1 m/s | 2.582 Pa | 42 | 0.018 Pa
177 | 158002 | 150.0 CMH | 160 mmø | 2.1 m/s | 2.582 Pa | 1011 | 0.442 Pa | 0.630 Pa
| 159196 | 150.0 CMH | 160 mmø | 2.1 m/s | 2.582 Pa | 137 | 0.060 Pa
| 159310 | 150.0 CMH | 160 mmø | 2.1 m/s | 2.582 Pa | 5 | 0.002 Pa
| 159367 | 150.0 CMH | 160 mmø | 2.1 m/s | 2.582 Pa | 82 | 0.036 Pa
| 159805 | 150.0 CMH | 160 mmø | 2.1 m/s | 2.582 Pa | 19 | 0.008 Pa
| 159829 | 150.0 CMH | 160 mmø | 2.1 m/s | 2.582 Pa | 188 | 0.082 Pa
178 | 156568 | 500.0 CMH | 250 mmø | 2.8 m/s | 4.814 Pa | 186 | 0.081 Pa | 1.106 Pa
| 159490 | 500.0 CMH | 250 mmø | 2.8 m/s | 4.814 Pa | 2344 | 1.025 Pa
179 | 1763102 | 300.0 CMH | 200 mm | 2.7 m/s | 4.231 Pa | 222 | 0.114 Pa | 0.114 Pa
181 | 156973 | 400.0 CMH | 250 mmø | 2.3 m/s | 3.081 Pa | 119 | 0.035 Pa | 0.676 Pa
| 157135 | 400.0 CMH | 250 mmø | 2.3 m/s | 3.081 Pa | 1863 | 0.546 Pa
| 157735 | 400.0 CMH | 250 mmø | 2.3 m/s | 3.081 Pa | 117 | 0.034 Pa
| 158989 | 400.0 CMH | 250 mmø | 2.3 m/s | 3.081 Pa | 162 | 0.047 Pa
| 159640 | 400.0 CMH | 250 mmø | 2.3 m/s | 3.081 Pa | 49 | 0.014 Pa
182 | 159733 | 400.0 CMH | 315 mmø | 1.4 m/s | 1.222 Pa | 30 | 0.003 Pa | 0.003 Pa
183 | 159271 | 1250.0 CMH | 315 mmø | 4.5 m/s | 11.937 Pa | 2650 | 1.975 Pa | 1.975 Pa
184 | 156178 | 1400.0 CMH | 315 mmø | 5.0 m/s | 14.974 Pa | 316 | 0.289 Pa | 4.785 Pa
| 156661 | 1400.0 CMH | 315 mmø | 5.0 m/s | 14.974 Pa | 2048 | 1.876 Pa
| 157126 | 1400.0 CMH | 315 mmø | 5.0 m/s | 14.974 Pa | 1696 | 1.554 Pa
| 157297 | 1400.0 CMH | 315 mmø | 5.0 m/s | 14.974 Pa | 485 | 0.445 Pa
| 157378 | 1400.0 CMH | 315 mmø | 5.0 m/s | 14.974 Pa | 486 | 0.445 Pa
| 159127 | 1400.0 CMH | 315 mmø | 5.0 m/s | 14.974 Pa | 68 | 0.062 Pa
| 159295 | 1400.0 CMH | 315 mmø | 5.0 m/s | 14.974 Pa | 124 | 0.113 Pa
185 | 156961 | 1550.0 CMH | 315 mmø | 5.5 m/s | 18.354 Pa | 815 | 0.899 Pa | 10.290 Pa
| 158431 | 1550.0 CMH | 315 mmø | 5.5 m/s | 18.354 Pa | 1616 | 1.783 Pa
| 158527 | 1550.0 CMH | 315 mmø | 5.5 m/s | 18.354 Pa | 5750 | 6.346 Pa
| 158773 | 1550.0 CMH | 315 mmø | 5.5 m/s | 18.354 Pa | 151 | 0.166 Pa
| 159826 | 1550.0 CMH | 315 mmø | 5.5 m/s | 18.354 Pa | 848 | 0.936 Pa
| 2647773 | 1550.0 CMH | 300 mmø | 5.5 m/s | 18.354 Pa | 137 | 0.158 Pa
187 | 156691 | 150.0 CMH | 160 mmø | 2.1 m/s | 2.582 Pa | 661 | 0.289 Pa | 1.323 Pa
| 156967 | 150.0 CMH | 160 mmø | 2.1 m/s | 2.582 Pa | 78 | 0.034 Pa
| 158095 | 150.0 CMH | 160 mmø | 2.1 m/s | 2.582 Pa | 329 | 0.144 Pa
| 158242 | 150.0 CMH | 160 mmø | 2.1 m/s | 2.582 Pa | 393 | 0.172 Pa
| 158926 | 150.0 CMH | 160 mmø | 2.1 m/s | 2.582 Pa | 216 | 0.094 Pa
| 159532 | 150.0 CMH | 160 mmø | 2.1 m/s | 2.582 Pa | 955 | 0.417 Pa
| 159679 | 150.0 CMH | 160 mmø | 2.1 m/s | 2.582 Pa | 212 | 0.092 Pa
| 159838 | 150.0 CMH | 160 mmø | 2.1 m/s | 2.582 Pa | 185 | 0.081 Pa
188 | 156301 | 350.0 CMH | 200 mmø | 3.1 m/s | 5.759 Pa | 268 | 0.182 Pa | 1.007 Pa
| 158203 | 350.0 CMH | 200 mmø | 3.1 m/s | 5.759 Pa | 139 | 0.095 Pa
| 158401 | 350.0 CMH | 200 mmø | 3.1 m/s | 5.759 Pa | 196 | 0.133 Pa
| 158611 | 350.0 CMH | 200 mmø | 3.1 m/s | 5.759 Pa | 239 | 0.163 Pa
| 158662 | 350.0 CMH | 200 mmø | 3.1 m/s | 5.759 Pa | 323 | 0.219 Pa
| 159286 | 350.0 CMH | 200 mmø | 3.1 m/s | 5.759 Pa | 317 | 0.215 Pa
189 | 156382 | 850.0 CMH | 250 mmø | 4.8 m/s | 13.912 Pa | 628 | 0.718 Pa | 12.025 Pa
| 156400 | 850.0 CMH | 250 mmø | 4.8 m/s | 13.912 Pa | 401 | 0.458 Pa
| 156940 | 850.0 CMH | 250 mmø | 4.8 m/s | 13.912 Pa | 1457 | 1.666 Pa
| 157357 | 850.0 CMH | 250 mmø | 4.8 m/s | 13.912 Pa | 964 | 1.102 Pa
| 157642 | 850.0 CMH | 250 mmø | 4.8 m/s | 13.912 Pa | 763 | 0.872 Pa
| 158740 | 850.0 CMH | 250 mmø | 4.8 m/s | 13.912 Pa | 763 | 0.872 Pa
| 159379 | 850.0 CMH | 250 mmø | 4.8 m/s | 13.912 Pa | 1441 | 1.647 Pa
| 159421 | 850.0 CMH | 250 mmø | 4.8 m/s | 13.912 Pa | 3827 | 4.377 Pa
| 159778 | 850.0 CMH | 250 mmø | 4.8 m/s | 13.912 Pa | 273 | 0.312 Pa
190 | 172972 | 125.0 CMH | 160 mmø | 1.7 m/s | 1.793 Pa | 144 | 0.046 Pa | 1.064 Pa
| 173017 | 125.0 CMH | 160 mmø | 1.7 m/s | 1.793 Pa | 926 | 0.292 Pa
| 174157 | 125.0 CMH | 160 mmø | 1.7 m/s | 1.793 Pa | 587 | 0.185 Pa
| 174607 | 125.0 CMH | 160 mmø | 1.7 m/s | 1.793 Pa | 59 | 0.019 Pa
| 175408 | 125.0 CMH | 160 mmø | 1.7 m/s | 1.793 Pa | 877 | 0.277 Pa
| 176119 | 125.0 CMH | 160 mmø | 1.7 m/s | 1.793 Pa | 397 | 0.125 Pa
| 176134 | 125.0 CMH | 160 mmø | 1.7 m/s | 1.793 Pa | 383 | 0.121 Pa
191 | 158932 | 125.0 CMH | 160 mmø | 1.7 m/s | 1.793 Pa | 3095 | 0.976 Pa | 1.076 Pa
| 2647551 | 125.0 CMH | 160 mm | 1.7 m/s | 1.793 Pa | 317 | 0.100 Pa
192 | 156844 | 250.0 CMH | 160 mmø | 3.5 m/s | 7.173 Pa | 164 | 0.180 Pa | 3.027 Pa
| 157786 | 250.0 CMH | 160 mmø | 3.5 m/s | 7.173 Pa | 2601 | 2.847 Pa
194 | 156688 | 350.0 CMH | 250 mmø | 2.0 m/s | 2.359 Pa | 1579 | 0.364 Pa | 0.585 Pa
| 157309 | 350.0 CMH | 250 mmø | 2.0 m/s | 2.359 Pa | 393 | 0.091 Pa
| 157942 | 350.0 CMH | 250 mmø | 2.0 m/s | 2.359 Pa | 283 | 0.065 Pa
| 158071 | 350.0 CMH | 250 mmø | 2.0 m/s | 2.359 Pa | 283 | 0.065 Pa
195 | 173197 | 125.0 CMH | 160 mmø | 1.7 m/s | 1.793 Pa | 45 | 0.014 Pa | 1.067 Pa
| 174079 | 125.0 CMH | 160 mmø | 1.7 m/s | 1.793 Pa | 177 | 0.056 Pa
| 1681110 | 125.0 CMH | 160 mmø | 1.7 m/s | 1.793 Pa | 3160 | 0.997 Pa
196 | 2647642 | 125.0 CMH | 160 mm | 1.7 m/s | 1.793 Pa | 263 | 0.083 Pa | 0.083 Pa
197 | 157360 | 100.0 CMH | 160 mmø | 1.4 m/s | 1.148 Pa | 137 | 0.029 Pa | 0.272 Pa
| 158116 | 100.0 CMH | 160 mmø | 1.4 m/s | 1.148 Pa | 19 | 0.004 Pa
| 158419 | 100.0 CMH | 160 mmø | 1.4 m/s | 1.148 Pa | 82 | 0.017 Pa
| 159184 | 100.0 CMH | 160 mmø | 1.4 m/s | 1.148 Pa | 193 | 0.041 Pa
| 159613 | 100.0 CMH | 160 mmø | 1.4 m/s | 1.148 Pa | 854 | 0.181 Pa
198 | 173071 | 100.0 CMH | 160 mmø | 1.4 m/s | 1.148 Pa | 45 | 0.010 Pa | 0.083 Pa
| 174433 | 100.0 CMH | 160 mmø | 1.4 m/s | 1.148 Pa | 27 | 0.006 Pa
| 174526 | 100.0 CMH | 160 mmø | 1.4 m/s | 1.148 Pa | 162 | 0.034 Pa
| 174826 | 100.0 CMH | 160 mmø | 1.4 m/s | 1.148 Pa | 158 | 0.033 Pa
199 | 156781 | 150.0 CMH | 160 mmø | 2.1 m/s | 2.582 Pa | 93 | 0.041 Pa | 0.361 Pa
| 157066 | 150.0 CMH | 160 mmø | 2.1 m/s | 2.582 Pa | 49 | 0.021 Pa
| 157435 | 150.0 CMH | 160 mmø | 2.1 m/s | 2.582 Pa | 48 | 0.021 Pa
| 157459 | 150.0 CMH | 160 mmø | 2.1 m/s | 2.582 Pa | 382 | 0.167 Pa
| 157795 | 150.0 CMH | 160 mmø | 2.1 m/s | 2.582 Pa | 173 | 0.075 Pa
| 159658 | 150.0 CMH | 160 mmø | 2.1 m/s | 2.582 Pa | 82 | 0.036 Pa
200 | 174553 | 125.0 CMH | 160 mmø | 1.7 m/s | 1.793 Pa | 275 | 0.087 Pa | 0.289 Pa
| 174619 | 125.0 CMH | 160 mmø | 1.7 m/s | 1.793 Pa | 46 | 0.014 Pa
| 175411 | 125.0 CMH | 160 mmø | 1.7 m/s | 1.793 Pa | 154 | 0.049 Pa
| 175855 | 125.0 CMH | 160 mmø | 1.7 m/s | 1.793 Pa | 440 | 0.139 Pa
201 | 174442 | 100.0 CMH | 160 mmø | 1.4 m/s | 1.148 Pa | 425 | 0.090 Pa | 0.373 Pa
| 175153 | 100.0 CMH | 160 mmø | 1.4 m/s | 1.148 Pa | 947 | 0.201 Pa
| 175480 | 100.0 CMH | 160 mmø | 1.4 m/s | 1.148 Pa | 115 | 0.024 Pa
| 1607397 | 100.0 CMH | 160 mm | 1.4 m/s | 1.148 Pa | 271 | 0.057 Pa
202 | 174145 | 100.0 CMH | 160 mmø | 1.4 m/s | 1.148 Pa | 947 | 0.201 Pa | 0.372 Pa
| 174943 | 100.0 CMH | 160 mmø | 1.4 m/s | 1.148 Pa | 425 | 0.090 Pa
| 175336 | 100.0 CMH | 160 mmø | 1.4 m/s | 1.148 Pa | 115 | 0.024 Pa
| 1607408 | 100.0 CMH | 160 mm | 1.4 m/s | 1.148 Pa | 271 | 0.057 Pa
203 | 173107 | 100.0 CMH | 160 mmø | 1.4 m/s | 1.148 Pa | 115 | 0.024 Pa | 0.373 Pa
| 175279 | 100.0 CMH | 160 mmø | 1.4 m/s | 1.148 Pa | 947 | 0.201 Pa
| 175921 | 100.0 CMH | 160 mmø | 1.4 m/s | 1.148 Pa | 425 | 0.090 Pa
| 1607432 | 100.0 CMH | 160 mm | 1.4 m/s | 1.148 Pa | 271 | 0.057 Pa
204 | 174115 | 100.0 CMH | 160 mmø | 1.4 m/s | 1.148 Pa | 994 | 0.211 Pa | 0.402 Pa
| 174346 | 100.0 CMH | 160 mmø | 1.4 m/s | 1.148 Pa | 520 | 0.110 Pa
| 176224 | 100.0 CMH | 160 mmø | 1.4 m/s | 1.148 Pa | 112 | 0.024 Pa
| 1607456 | 100.0 CMH | 160 mm | 1.4 m/s | 1.148 Pa | 270 | 0.057 Pa
205 | 157432 | 250.0 CMH | 250 mmø | 1.4 m/s | 1.203 Pa | 167 | 0.021 Pa | 0.061 Pa
| 159091 | 250.0 CMH | 250 mmø | 1.4 m/s | 1.203 Pa | 317 | 0.040 Pa
206 | 156745 | 500.0 CMH | 250 mmø | 2.8 m/s | 4.814 Pa | 385 | 0.168 Pa | 0.917 Pa
| 158152 | 500.0 CMH | 250 mmø | 2.8 m/s | 4.814 Pa | 99 | 0.043 Pa
| 159199 | 500.0 CMH | 250 mmø | 2.8 m/s | 4.814 Pa | 434 | 0.190 Pa
| 159550 | 500.0 CMH | 250 mmø | 2.8 m/s | 4.814 Pa | 714 | 0.312 Pa
| 460715 | 500.0 CMH | 250 mmø | 2.8 m/s | 4.814 Pa | 330 | 0.144 Pa
| 2304829 | 500.0 CMH | 250 mmø | 2.8 m/s | 4.814 Pa | 135 | 0.059 Pa
207 | 156832 | 250.0 CMH | 250 mmø | 1.4 m/s | 1.203 Pa | 209 | 0.026 Pa | 0.367 Pa
| 157537 | 250.0 CMH | 250 mmø | 1.4 m/s | 1.203 Pa | 1382 | 0.175 Pa
| 158302 | 250.0 CMH | 250 mmø | 1.4 m/s | 1.203 Pa | 521 | 0.066 Pa
| 2647401 | 250.0 CMH | 250 mm | 1.4 m/s | 1.203 Pa | 789 | 0.100 Pa
208 | 158359 | 100.0 CMH | 160 mmø | 1.4 m/s | 1.148 Pa | 107 | 0.023 Pa | 0.474 Pa
| 461448 | 100.0 CMH | 160 mm | 1.4 m/s | 1.148 Pa | 368 | 0.078 Pa
| 2500040 | 100.0 CMH | 160 mmø | 1.4 m/s | 1.148 Pa | 600 | 0.127 Pa
| 2500049 | 100.0 CMH | 160 mmø | 1.4 m/s | 1.148 Pa | 963 | 0.204 Pa
| 2500085 | 100.0 CMH | 160 mmø | 1.4 m/s | 1.148 Pa | 197 | 0.042 Pa
209 | 190426 | 100.0 CMH | 200 mmx200 mm | 0.7 m/s | 0.290 Pa | 339 | 0.016 Pa | 0.018 Pa
| 893507 | 100.0 CMH | 200 mmx200 mm | 0.7 m/s | 0.290 Pa | 46 | 0.002 Pa
Fitting and Accessory Loss Coefficient Summary by Sections
Section | Element ID | Loss Method | ASHRAE Table | Loss Coefficient | Pressure Loss | Total Pressure Loss
1 | 1601679 | Coefficient from ASHRAE Table | SD5-24 | 4.4 | 5.295 Pa | 5.295 Pa
| 1601712 | Coefficient from ASHRAE Table | - | 0 | 0.000 Pa
2 | 1589342 | Specific Loss | - | 0.16619 | 0.800 Pa | 73.637 Pa
| 1589405 | Coefficient from ASHRAE Table | SD5-24 | 3.9638 | 19.081 Pa
| 1589605 | Coefficient from ASHRAE Table | CD6-4 | 0.24 | 1.155 Pa
| 1589606 | Specific Loss | - | 6.232 | 30.000 Pa
| 1601625 | Specific Loss | - | 0.16619 | 0.800 Pa
| 1601629 | Coefficient from ASHRAE Table | - | 0 | 0.000 Pa
| 1601649 | Coefficient from ASHRAE Table | - | 0 | 0.000 Pa
| 1601675 | Specific Loss | - | 0.16619 | 0.800 Pa
| 1601679 | Coefficient from ASHRAE Table | SD5-24 | 4.3624 | 21.000 Pa
3 | 1589325 | Coefficient from ASHRAE Table | CD3-11 | 0 | 0.000 Pa | 35.514 Pa
| 1589329 | Specific Loss | - | 0.098335 | 0.800 Pa
| 1589333 | Specific Loss | - | 0.098335 | 0.800 Pa
| 1589405 | Coefficient from ASHRAE Table | SD5-24 | 2.5813 | 21.000 Pa
| 2305159 | Coefficient from ASHRAE Table | SR5-11 | 1.5873 | 12.914 Pa
4 | 2305159 | Coefficient from ASHRAE Table | SR5-11 | 0 | 0.000 Pa | 0.000 Pa
| 1577090 | Coefficient from ASHRAE Table | - | 0 | 0.000 Pa
5 | 1577090 | Coefficient from ASHRAE Table | - | 0 | 0.000 Pa | 0.510 Pa
| 2305083 | Coefficient from ASHRAE Table | SR5-11 | 0.063835 | 0.510 Pa
6 | 2305083 | Coefficient from ASHRAE Table | SR5-11 | 0 | 0.000 Pa | 14.225 Pa
| 1588078 | Coefficient from ASHRAE Table | CR6-3 | 0 | 0.000 Pa
| 1588082 | Coefficient from ASHRAE Table | CR6-3 | 0 | 0.000 Pa
| 2159001 | Coefficient from ASHRAE Table | SR5-11 | 1.4214 | 14.225 Pa
7 | 2159001 | Coefficient from ASHRAE Table | SR5-11 | 0 | 0.000 Pa | 0.346 Pa
| 1885528 | Coefficient from ASHRAE Table | SR4-2 | 0.042778 | 0.346 Pa
8 | 2156961 | Coefficient from ASHRAE Table | SR5-11 | 0.45331 | 1.767 Pa | 1.767 Pa
| 1885528 | Coefficient from ASHRAE Table | SR4-2 | 0 | 0.000 Pa
9 | 2156961 | Coefficient from ASHRAE Table | SR5-11 | 0 | 0.000 Pa | 40.410 Pa
| 819759 | Coefficient from ASHRAE Table | SR3-1 | 1.15 | 12.004 Pa
| 820116 | Coefficient from ASHRAE Table | CR3-1 | 0.10374 | 1.083 Pa
| 1190855 | Coefficient from ASHRAE Table | CR6-3 | 0 | 0.000 Pa
| 1931033 | Coefficient from ASHRAE Table | CR3-1 | 0.10374 | 1.083 Pa
| 1931098 | Coefficient from ASHRAE Table | SR3-1 | 1.15 | 12.004 Pa
| 2156685 | Coefficient from ASHRAE Table | SR5-11 | 1.364 | 14.238 Pa
10 | 2156685 | Coefficient from ASHRAE Table | SR5-11 | 0 | 0.000 Pa | 27.084 Pa
| 819793 | Coefficient from ASHRAE Table | SR3-1 | 1.15 | 8.605 Pa
| 819980 | Coefficient from ASHRAE Table | SR3-1 | 1.15 | 8.605 Pa
| 819990 | Coefficient from ASHRAE Table | SR3-1 | 1.15 | 8.605 Pa
| 1930970 | Coefficient from ASHRAE Table | SR4-2 | 0.16948 | 1.268 Pa
11 | 1930970 | Coefficient from ASHRAE Table | SR4-2 | 0 | 0.000 Pa | 0.000 Pa
12 | 1601679 | Coefficient from ASHRAE Table | SD5-24 | 4.4 | 5.295 Pa | 6.095 Pa
| 1601723 | Coefficient from ASHRAE Table | - | 0 | 0.000 Pa
| 2304410 | Specific Loss | - | 0.66475 | 0.800 Pa
13 | 1803544 | Specific Loss | - | 0.17426 | 0.800 Pa | 208.157 Pa
| 1803689 | Specific Loss | - | 0.17426 | 0.800 Pa
| 1803694 | Coefficient from ASHRAE Table | SD5-24 | 5.7847 | 26.557 Pa
| 1806139 | Specific Loss | - | 6.5347 | 30.000 Pa
| 1806140 | Specific Loss | - | 32.6737 | 150.000 Pa
14 | 1803496 | Specific Loss | - | 0.049433 | 0.800 Pa | 22.426 Pa
| 1803499 | Specific Loss | - | 0.049433 | 0.800 Pa
| 1803694 | Coefficient from ASHRAE Table | SD5-24 | 0 | 0.000 Pa
| 2159430 | Coefficient from ASHRAE Table | SR5-11 | 1.2336 | 19.965 Pa
| 2159433 | Coefficient from ASHRAE Table | - | 0 | 0.000 Pa
| 2159438 | Coefficient from ASHRAE Table | - | 0 | 0.000 Pa
| 2159484 | Coefficient from ASHRAE Table | CD3-11 | 0 | 0.000 Pa
| 2159502 | Coefficient from ASHRAE Table | CD3-11 | 0.053255 | 0.862 Pa
15 | 2159430 | Coefficient from ASHRAE Table | SR5-11 | 0 | 0.000 Pa | 1.663 Pa
| 1830617 | Coefficient from ASHRAE Table | CR3-1 | 0.086706 | 0.831 Pa
| 1830680 | Coefficient from ASHRAE Table | CR3-1 | 0.086706 | 0.831 Pa
| 1830723 | Coefficient from ASHRAE Table | CR6-3 | 0 | 0.000 Pa
| 1830868 | Coefficient from ASHRAE Table | - | 0 | 0.000 Pa
16 | 1830868 | Coefficient from ASHRAE Table | - | 0 | 0.000 Pa | 0.356 Pa
| 2159242 | Coefficient from ASHRAE Table | SR5-11 | 0.059412 | 0.356 Pa
17 | 2159175 | Coefficient from ASHRAE Table | SR3-1 | 1.15 | 8.461 Pa | 23.255 Pa
| 2159178 | Coefficient from ASHRAE Table | SR5-11 | 2.0108 | 14.794 Pa
| 2159242 | Coefficient from ASHRAE Table | SR5-11 | 0 | 0.000 Pa
18 | 2159178 | Coefficient from ASHRAE Table | SR5-11 | 0 | 0.000 Pa | 11.867 Pa
| 819887 | Coefficient from ASHRAE Table | SR4-2 | 0.0024 | 0.025 Pa
| 1920526 | Coefficient from ASHRAE Table | SR3-1 | 1.15 | 11.843 Pa
| 1920543 | Coefficient from ASHRAE Table | CR6-3 | 0 | 0.000 Pa
19 | 819795 | Coefficient from ASHRAE Table | SR3-1 | 1.21 | 11.967 Pa | 46.583 Pa
| 819887 | Coefficient from ASHRAE Table | SR4-2 | 0 | 0.000 Pa
| 1009474 | Coefficient from ASHRAE Table | CR3-1 | 0.078365 | 0.775 Pa
| 1009477 | Coefficient from ASHRAE Table | CR3-1 | 0.078365 | 0.775 Pa
| 1920552 | Coefficient from ASHRAE Table | SR3-1 | 1.21 | 11.967 Pa
| 1920554 | Coefficient from ASHRAE Table | SR3-1 | 1.0667 | 10.549 Pa
| 1920558 | Coefficient from ASHRAE Table | SR3-1 | 1.0667 | 10.549 Pa
| 1920587 | Coefficient from ASHRAE Table | - | 0 | 0.000 Pa
20 | 1920587 | Coefficient from ASHRAE Table | - | 0 | 0.000 Pa | 0.727 Pa
| 1920637 | Coefficient from ASHRAE Table | SR4-1 | 0.073512 | 0.727 Pa
21 | 1920637 | Coefficient from ASHRAE Table | SR4-1 | 0 | 0.000 Pa | 1.504 Pa
| 2156685 | Coefficient from ASHRAE Table | SR5-11 | 0.60841 | 1.504 Pa
22 | 461481 | Specific Loss | - | 130.6948 | 150.000 Pa | 157.002 Pa
| 461487 | Specific Loss | - | 0.69704 | 0.800 Pa
| 461489 | Coefficient from ASHRAE Table | - | 0 | 0.000 Pa
| 2174119 | Specific Loss | - | 0.69704 | 0.800 Pa
| 2174264 | Coefficient from ASHRAE Table | SR5-11 | 4.7066 | 5.402 Pa
23 | 2174089 | Coefficient from ASHRAE Table | SR5-11 | 0.12 | 0.557 Pa | 0.557 Pa
| 2174264 | Coefficient from ASHRAE Table | SR5-11 | 0 | 0.000 Pa
24 | 2174089 | Coefficient from ASHRAE Table | SR5-11 | 0 | 0.000 Pa | 0.000 Pa
| 893531 | Coefficient from ASHRAE Table | - | 0 | 0.000 Pa
25 | 893531 | Coefficient from ASHRAE Table | - | 0 | 0.000 Pa | 8.695 Pa
| 893557 | Coefficient from ASHRAE Table | SR3-1 | 1.15 | 8.337 Pa
| 893682 | Coefficient from ASHRAE Table | SR4-2 | 0.04932 | 0.358 Pa
26 | 893578 | Coefficient from ASHRAE Table | CR6-3 | 10.103 | 30.000 Pa | 31.343 Pa
| 893682 | Coefficient from ASHRAE Table | SR4-2 | 0 | 0.000 Pa
| 893780 | Coefficient from ASHRAE Table | SR4-2 | 0.45225 | 1.343 Pa
27 | 893780 | Coefficient from ASHRAE Table | SR4-2 | 0 | 0.000 Pa | 21.067 Pa
| 893800 | Coefficient from ASHRAE Table | CR6-3 | 0 | 0.000 Pa
| 894115 | Coefficient from ASHRAE Table | CR3-1 | 0.067616 | 0.490 Pa
| 894117 | Coefficient from ASHRAE Table | CR3-17 | 2.1434 | 15.539 Pa
| 2174020 | Coefficient from ASHRAE Table | SR5-1 | 0.69491 | 5.038 Pa
28 | 1517502 | Coefficient from ASHRAE Table | - | 0 | 0.000 Pa | 0.000 Pa
| 2174020 | Coefficient from ASHRAE Table | SR5-1 | 0 | 0.000 Pa
29 | 1517502 | Coefficient from ASHRAE Table | - | 0 | 0.000 Pa | 0.000 Pa
| 1517508 | Coefficient from ASHRAE Table | - | 0 | 0.000 Pa
30 | 1517508 | Coefficient from ASHRAE Table | - | 0 | 0.000 Pa | 0.000 Pa
| 1517513 | Coefficient from ASHRAE Table | - | 0 | 0.000 Pa
31 | 1517513 | Coefficient from ASHRAE Table | - | 0 | 0.000 Pa | 3.018 Pa
| 1517518 | Coefficient from ASHRAE Table | CR3-1 | 0.12974 | 1.509 Pa
| 1517520 | Coefficient from ASHRAE Table | CR3-1 | 0.12974 | 1.509 Pa
| 1517522 | Coefficient from ASHRAE Table | - | 0 | 0.000 Pa
32 | 1517522 | Coefficient from ASHRAE Table | - | 0 | 0.000 Pa | 0.000 Pa
| 1517527 | Coefficient from ASHRAE Table | - | 0 | 0.000 Pa
33 | 1517527 | Coefficient from ASHRAE Table | - | 0 | 0.000 Pa | 13.842 Pa
| 1517531 | Coefficient from ASHRAE Table | SR3-1 | 1.19 | 13.842 Pa
| 1517536 | Coefficient from ASHRAE Table | - | 0 | 0.000 Pa
34 | 1517536 | Coefficient from ASHRAE Table | - | 0 | 0.000 Pa | 14.656 Pa
| 1517550 | Coefficient from ASHRAE Table | SR3-1 | 1.19 | 13.842 Pa
| 1517553 | Coefficient from ASHRAE Table | SR4-2 | 0.07 | 0.814 Pa
35 | 1517553 | Coefficient from ASHRAE Table | SR4-2 | 0 | 0.000 Pa | 6.752 Pa
| 1517595 | Coefficient from ASHRAE Table | CR3-17 | 0.93663 | 2.724 Pa
| 1517597 | Coefficient from ASHRAE Table | CR3-17 | 0.46102 | 1.341 Pa
| 1619088 | Coefficient from ASHRAE Table | CR6-3 | 0 | 0.000 Pa
| 1619091 | Coefficient from ASHRAE Table | CR6-3 | 0 | 0.000 Pa
| 1635626 | Coefficient from ASHRAE Table | CR3-17 | 0.46222 | 1.344 Pa
| 1635770 | Coefficient from ASHRAE Table | CR3-17 | 0.46222 | 1.344 Pa
| 2615108 | Coefficient from ASHRAE Table | - | 0 | 0.000 Pa
36 | 1588131 | Coefficient from ASHRAE Table | SR4-2 | 0.054959 | 0.153 Pa | 3.362 Pa
| 1620055 | Coefficient from ASHRAE Table | SR3-1 | 1.15 | 3.209 Pa
| 2615108 | Coefficient from ASHRAE Table | - | 0 | 0.000 Pa
37 | 1588131 | Coefficient from ASHRAE Table | SR4-2 | 0 | 0.000 Pa | 3.813 Pa
| 2159001 | Coefficient from ASHRAE Table | SR5-11 | 5.6912 | 3.813 Pa
38 | 1722670 | Specific Loss | - | 0.69704 | 0.800 Pa | 188.779 Pa
| 1734172 | Specific Loss | - | 0.69704 | 0.800 Pa
| 1734174 | Specific Loss | - | 26.139 | 30.000 Pa
| 1734175 | Specific Loss | - | 130.6948 | 150.000 Pa
| 2158723 | Coefficient from ASHRAE Table | SR5-11 | 6.2548 | 7.179 Pa
39 | 2158723 | Coefficient from ASHRAE Table | SR5-11 | 0 | 0.000 Pa | 8.337 Pa
| 1775432 | Coefficient from ASHRAE Table | SR3-1 | 1.15 | 8.337 Pa
| 1775453 | Coefficient from ASHRAE Table | - | 0 | 0.000 Pa
40 | 1775453 | Coefficient from ASHRAE Table | - | 0 | 0.000 Pa | 30.000 Pa
| 1775459 | Coefficient from ASHRAE Table | CR6-3 | 10.103 | 30.000 Pa
| 1775460 | Coefficient from ASHRAE Table | - | 0 | 0.000 Pa
41 | 273163 | Coefficient from ASHRAE Table | CR6-3 | 0 | 0.000 Pa | 0.000 Pa
| 1775460 | Coefficient from ASHRAE Table | - | 0 | 0.000 Pa
| 1775484 | Coefficient from ASHRAE Table | - | 0 | 0.000 Pa
42 | 1775484 | Coefficient from ASHRAE Table | - | 0 | 0.000 Pa | 54.794 Pa
| 1775491 | Coefficient from ASHRAE Table | CR3-17 | 4.3817 | 31.765 Pa
| 1775495 | Coefficient from ASHRAE Table | CR3-1 | 0.099515 | 0.721 Pa
| 1775524 | Coefficient from ASHRAE Table | SR3-1 | 1.15 | 8.337 Pa
| 2158600 | Coefficient from ASHRAE Table | SR5-11 | 1.927 | 13.970 Pa
43 | 2158377 | Coefficient from ASHRAE Table | SR5-11 | 0.062077 | 0.601 Pa | 0.601 Pa
| 2158600 | Coefficient from ASHRAE Table | SR5-11 | 0 | 0.000 Pa
44 | 2158377 | Coefficient from ASHRAE Table | SR5-11 | 0 | 0.000 Pa | 39.636 Pa
| 1763037 | Coefficient from ASHRAE Table | CR3-17 | 0.81615 | 9.826 Pa
| 1763050 | Coefficient from ASHRAE Table | CR3-1 | 0.11469 | 1.381 Pa
| 1763058 | Coefficient from ASHRAE Table | SR3-1 | 1.15 | 13.846 Pa
| 1793494 | Coefficient from ASHRAE Table | SR3-1 | 1.15 | 13.846 Pa
| 1793579 | Coefficient from ASHRAE Table | SR4-2 | 0.06125 | 0.737 Pa
45 | 1793579 | Coefficient from ASHRAE Table | SR4-2 | 0 | 0.000 Pa | 0.531 Pa
| 2157848 | Coefficient from ASHRAE Table | SR5-11 | 0.13949 | 0.531 Pa
46 | 2157848 | Coefficient from ASHRAE Table | SR5-11 | 0 | 0.000 Pa | 0.443 Pa
| 2157503 | Coefficient from ASHRAE Table | SR5-11 | 0.071435 | 0.443 Pa
47 | 2157503 | Coefficient from ASHRAE Table | SR5-11 | 0 | 0.000 Pa | 15.116 Pa
| 1829523 | Coefficient from ASHRAE Table | CR6-3 | 0 | 0.000 Pa
| 1829531 | Coefficient from ASHRAE Table | CR6-3 | 0 | 0.000 Pa
| 2156961 | Coefficient from ASHRAE Table | SR5-11 | 1.8916 | 15.116 Pa
48 | 1775539 | Specific Loss | - | 58.0866 | 150.000 Pa | 194.819 Pa
| 1775552 | Specific Loss | - | 0.30979 | 0.800 Pa
| 1775556 | Specific Loss | - | 11.6173 | 30.000 Pa
| 1775568 | Specific Loss | - | 0.30979 | 0.800 Pa
| 2158377 | Coefficient from ASHRAE Table | SR5-11 | 5.1189 | 13.219 Pa
| 2158399 | Coefficient from ASHRAE Table | CD3-11 | 0 | 0.000 Pa
49 | 1784782 | Specific Loss | - | 0.69704 | 0.800 Pa | 193.643 Pa
| 1784787 | Specific Loss | - | 0.69704 | 0.800 Pa
| 1784789 | Specific Loss | - | 0.69704 | 0.800 Pa
| 1784793 | Specific Loss | - | 26.139 | 30.000 Pa
| 1784794 | Specific Loss | - | 130.6948 | 150.000 Pa
| 1784795 | Coefficient from ASHRAE Table | - | 0 | 0.000 Pa
| 1784804 | Specific Loss | - | 0.69704 | 0.800 Pa
| 1784807 | Coefficient from ASHRAE Table | - | 0 | 0.000 Pa
| 1784821 | Coefficient from ASHRAE Table | SD5-24 | 9.0991 | 10.443 Pa
50 | 1784821 | Coefficient from ASHRAE Table | SD5-24 | 0 | 0.000 Pa | 48.520 Pa
| 2290758 | Coefficient from ASHRAE Table | SD5-24 | 6.9995 | 48.520 Pa
51 | 1784971 | Coefficient from ASHRAE Table | SD5-24 | 5.8841 | 63.732 Pa | 63.732 Pa
| 2290758 | Coefficient from ASHRAE Table | SD5-24 | 0 | 0.000 Pa
52 | 1784971 | Coefficient from ASHRAE Table | SD5-24 | 0 | 0.000 Pa | 0.000 Pa
| 1803423 | Coefficient from ASHRAE Table | - | 0 | 0.000 Pa
53 | 2159757 | Coefficient from ASHRAE Table | SR5-11 | 0.09 | 0.372 Pa | 0.372 Pa
| 1803423 | Coefficient from ASHRAE Table | - | 0 | 0.000 Pa
54 | 2159757 | Coefficient from ASHRAE Table | SR5-11 | 0 | 0.000 Pa | 0.448 Pa
| 2159643 | Coefficient from ASHRAE Table | SR5-11 | 0.078261 | 0.448 Pa
55 | 2159643 | Coefficient from ASHRAE Table | SR5-11 | 0 | 0.000 Pa | 2.255 Pa
| 1829936 | Coefficient from ASHRAE Table | SR4-2 | 0.29767 | 2.255 Pa
56 | 1829936 | Coefficient from ASHRAE Table | SR4-2 | 0 | 0.000 Pa | 15.045 Pa
| 1829939 | Coefficient from ASHRAE Table | SR3-1 | 1.2014 | 15.045 Pa
| 1829944 | Coefficient from ASHRAE Table | - | 0 | 0.000 Pa
57 | 1829942 | Coefficient from ASHRAE Table | - | 0 | 0.000 Pa | 0.000 Pa
| 1829944 | Coefficient from ASHRAE Table | - | 0 | 0.000 Pa
58 | 1829942 | Coefficient from ASHRAE Table | - | 0 | 0.000 Pa | 0.665 Pa
| 1830005 | Coefficient from ASHRAE Table | SR4-2 | 0.053126 | 0.665 Pa
59 | 1830005 | Coefficient from ASHRAE Table | SR4-2 | 0 | 0.000 Pa | 8.301 Pa
| 1830073 | Coefficient from ASHRAE Table | SR3-1 | 1.15 | 2.756 Pa
| 1830203 | Coefficient from ASHRAE Table | SR3-1 | 1.15 | 2.756 Pa
| 1830407 | Coefficient from ASHRAE Table | CR3-1 | 0.086706 | 0.208 Pa
| 1830531 | Coefficient from ASHRAE Table | CR3-1 | 0.086706 | 0.208 Pa
| 2159430 | Coefficient from ASHRAE Table | SR5-11 | 0.99 | 2.373 Pa
60 | 390937 | Coefficient from ASHRAE Table | SD5-24 | 4.4 | 11.362 Pa | 12.962 Pa
| 1269058 | Specific Loss | - | 0.30979 | 0.800 Pa
| 1269065 | Specific Loss | - | 0.30979 | 0.800 Pa
61 | 390934 | Specific Loss | - | 0.077449 | 0.800 Pa | 184.000 Pa
| 390937 | Coefficient from ASHRAE Table | SD5-24 | 0 | 0.000 Pa
| 407943 | Specific Loss | - | 14.5216 | 150.000 Pa
| 407944 | Specific Loss | - | 2.9043 | 30.000 Pa
| 407972 | Specific Loss | - | 0.077449 | 0.800 Pa
| 407974 | Specific Loss | - | 0.077449 | 0.800 Pa
| 962982 | Coefficient from ASHRAE Table | - | 0 | 0.000 Pa
| 1268986 | Specific Loss | - | 0.077449 | 0.800 Pa
| 1268991 | Specific Loss | - | 0.077449 | 0.800 Pa
| 1517484 | Coefficient from ASHRAE Table | - | 0 | 0.000 Pa
62 | 962982 | Coefficient from ASHRAE Table | - | 0 | 0.000 Pa | 0.087 Pa
| 962985 | Coefficient from ASHRAE Table | SR4-1 | 0.033333 | 0.087 Pa
63 | 2173897 | Coefficient from ASHRAE Table | SR5-11 | 0.32 | 0.371 Pa | 0.371 Pa
| 962985 | Coefficient from ASHRAE Table | SR4-1 | 0 | 0.000 Pa
64 | 2174020 | Coefficient from ASHRAE Table | SR5-1 | 0.35053 | 0.915 Pa | 0.915 Pa
| 2173897 | Coefficient from ASHRAE Table | SR5-11 | 0 | 0.000 Pa
65 | 1722667 | Specific Loss | - | 0.69704 | 0.800 Pa | 187.002 Pa
| 1734159 | Specific Loss | - | 0.69704 | 0.800 Pa
| 1734161 | Specific Loss | - | 26.139 | 30.000 Pa
| 1734162 | Specific Loss | - | 130.6948 | 150.000 Pa
| 1734192 | Coefficient from ASHRAE Table | - | 0 | 0.000 Pa
| 2158767 | Coefficient from ASHRAE Table | SR5-11 | 4.7066 | 5.402 Pa
66 | 2158767 | Coefficient from ASHRAE Table | SR5-11 | 0 | 0.000 Pa | 0.557 Pa
| 2158723 | Coefficient from ASHRAE Table | SR5-11 | 0.12 | 0.557 Pa
67 | 1722655 | Specific Loss | - | 0.69704 | 0.800 Pa | 183.425 Pa
| 1734092 | Specific Loss | - | 0.69704 | 0.800 Pa
| 1734095 | Specific Loss | - | 26.139 | 30.000 Pa
| 1734096 | Specific Loss | - | 130.6948 | 150.000 Pa
| 1734141 | Coefficient from ASHRAE Table | - | 0 | 0.000 Pa
| 2158856 | Coefficient from ASHRAE Table | SR5-11 | 1.5901 | 1.825 Pa
68 | 2158856 | Coefficient from ASHRAE Table | SR5-11 | 0 | 0.000 Pa | 0.371 Pa
| 2158819 | Coefficient from ASHRAE Table | SR5-11 | 0.32 | 0.371 Pa
69 | 2158819 | Coefficient from ASHRAE Table | SR5-11 | 0 | 0.000 Pa | 0.470 Pa
| 2158767 | Coefficient from ASHRAE Table | SR5-11 | 0.18 | 0.470 Pa
70 | 1772598 | Coefficient from ASHRAE Table | SD5-24 | 7.0119 | 18.107 Pa | 202.107 Pa
| 1775348 | Specific Loss | - | 0.30979 | 0.800 Pa
| 1775354 | Specific Loss | - | 58.0866 | 150.000 Pa
| 1775355 | Specific Loss | - | 11.6173 | 30.000 Pa
| 1775368 | Specific Loss | - | 0.30979 | 0.800 Pa
| 1775371 | Specific Loss | - | 0.30979 | 0.800 Pa
| 1775374 | Specific Loss | - | 0.30979 | 0.800 Pa
| 1775377 | Coefficient from ASHRAE Table | - | 0 | 0.000 Pa
| 1775380 | Specific Loss | - | 0.30979 | 0.800 Pa
71 | 1772598 | Coefficient from ASHRAE Table | SD5-24 | 0 | 0.000 Pa | 67.958 Pa
| 1803547 | Specific Loss | - | 0.072437 | 0.800 Pa
| 1803674 | Specific Loss | - | 0.072437 | 0.800 Pa
| 1803676 | Specific Loss | - | 0.072437 | 0.800 Pa
| 1803694 | Coefficient from ASHRAE Table | SD5-24 | 5.8637 | 64.758 Pa
| 2290990 | Specific Loss | - | 0.072437 | 0.800 Pa
72 | 1722649 | Specific Loss | - | 0.69704 | 0.800 Pa | 182.400 Pa
| 1722878 | Specific Loss | - | 0.69704 | 0.800 Pa
| 1722913 | Specific Loss | - | 0.69704 | 0.800 Pa
| 1723049 | Specific Loss | - | 26.139 | 30.000 Pa
| 1723073 | Specific Loss | - | 130.6948 | 150.000 Pa
| 1734129 | Coefficient from ASHRAE Table | - | 0 | 0.000 Pa
73 | 1734129 | Coefficient from ASHRAE Table | - | 0 | 0.000 Pa | 0.287 Pa
| 2158856 | Coefficient from ASHRAE Table | SR5-11 | 0.99 | 0.287 Pa
74 | 1684948 | Specific Loss | - | 0.66475 | 0.800 Pa | 41.500 Pa
| 1684951 | Coefficient from ASHRAE Table | CD6-4 | 0.24 | 0.289 Pa
| 1684952 | Specific Loss | - | 24.928 | 30.000 Pa
| 1684962 | Coefficient from ASHRAE Table | CD3-11 | 0 | 0.000 Pa
| 2305083 | Coefficient from ASHRAE Table | SR5-11 | 8.6514 | 10.412 Pa
75 | 1589405 | Coefficient from ASHRAE Table | SD5-24 | 4.4881 | 11.590 Pa | 193.990 Pa
| 1589457 | Coefficient from ASHRAE Table | - | 0 | 0.000 Pa
| 1589484 | Specific Loss | - | 0.30979 | 0.800 Pa
| 1589488 | Specific Loss | - | 0.30979 | 0.800 Pa
| 1589539 | Specific Loss | - | 58.0866 | 150.000 Pa
| 1589540 | Specific Loss | - | 11.6173 | 30.000 Pa
| 1589552 | Specific Loss | - | 0.30979 | 0.800 Pa
76 | 1746540 | Specific Loss | - | 0.66475 | 0.800 Pa | 40.543 Pa
| 1746557 | Specific Loss | - | 24.928 | 30.000 Pa
| 1746661 | Coefficient from ASHRAE Table | CD6-4 | 0.24 | 0.289 Pa
| 2157503 | Coefficient from ASHRAE Table | SR5-11 | 7.8561 | 9.454 Pa
| 2157607 | Coefficient from ASHRAE Table | CD3-11 | 0 | 0.000 Pa
77 | 1514025 | Specific Loss | - | 0.17426 | 0.800 Pa | 18.143 Pa
| 1514028 | Specific Loss | - | 0.17426 | 0.800 Pa
| 1514031 | Coefficient from ASHRAE Table | - | 0 | 0.000 Pa
| 1514042 | Coefficient from ASHRAE Table | SD5-24 | 3.6035 | 16.543 Pa
78 | 1513989 | Specific Loss | - | 0.069783 | 0.800 Pa | 34.256 Pa
| 1513995 | Specific Loss | - | 0.069783 | 0.800 Pa
| 1514001 | Specific Loss | - | 0.069783 | 0.800 Pa
| 1514004 | Specific Loss | - | 0.069783 | 0.800 Pa
| 1514034 | Specific Loss | - | 0.069783 | 0.800 Pa
| 1514042 | Coefficient from ASHRAE Table | SD5-24 | 1.8318 | 21.000 Pa
| 1514059 | Coefficient from ASHRAE Table | CD6-4 | 0.24 | 2.751 Pa
| 1514060 | Coefficient from ASHRAE Table | CD6-4 | 0.24 | 2.751 Pa
| 1722163 | Specific Loss | - | 0.069783 | 0.800 Pa
| 1722168 | Coefficient from ASHRAE Table | - | 0 | 0.000 Pa
| 1722171 | Specific Loss | - | 0.069783 | 0.800 Pa
| 1722174 | Specific Loss | - | 0.069783 | 0.800 Pa
| 1722177 | Specific Loss | - | 0.069783 | 0.800 Pa
| 1722182 | Coefficient from ASHRAE Table | - | 0 | 0.000 Pa
| 1722185 | Coefficient from ASHRAE Table | SD4-1 | 0.048275 | 0.553 Pa
79 | 1722185 | Coefficient from ASHRAE Table | SD4-1 | 0 | 0.000 Pa | 13.556 Pa
| 1722188 | Coefficient from ASHRAE Table | SD5-24 | 4.4 | 13.556 Pa
80 | 1722188 | Coefficient from ASHRAE Table | SD5-24 | 1.7041 | 21.000 Pa | 23.650 Pa
| 1772531 | Specific Loss | - | 0.064917 | 0.800 Pa
| 1772534 | Specific Loss | - | 0.064917 | 0.800 Pa
| 1772552 | Specific Loss | - | 0.064917 | 0.800 Pa
| 1772557 | Coefficient from ASHRAE Table | - | 0 | 0.000 Pa
| 1772575 | Coefficient from ASHRAE Table | SD4-1 | 0.020281 | 0.250 Pa
81 | 1772575 | Coefficient from ASHRAE Table | SD4-1 | 0 | 0.000 Pa | 51.993 Pa
| 1772598 | Coefficient from ASHRAE Table | SD5-24 | 6.6387 | 51.993 Pa
82 | 1722118 | Specific Loss | - | 0.58454 | 0.800 Pa | 12.302 Pa
| 2292088 | Coefficient from ASHRAE Table | SD5-10 | 7.82 | 10.702 Pa
| 2292113 | Specific Loss | - | 0.58454 | 0.800 Pa
83 | 1742927 | Specific Loss | - | 0.064949 | 0.800 Pa | 10.574 Pa
| 1742930 | Coefficient from ASHRAE Table | - | 0 | 0.000 Pa
| 1742945 | Specific Loss | - | 0.064949 | 0.800 Pa
| 1742959 | Specific Loss | - | 0.064949 | 0.800 Pa
| 1742962 | Coefficient from ASHRAE Table | - | 0 | 0.000 Pa
| 1784692 | Coefficient from ASHRAE Table | SD4-1 | 0.66362 | 8.174 Pa
| 2292088 | Coefficient from ASHRAE Table | SD5-10 | 0 | 0.000 Pa
84 | 1784668 | Coefficient from ASHRAE Table | SD4-2 | 0.057925 | 1.742 Pa | 181.742 Pa
| 1784682 | Specific Loss | - | 4.9881 | 150.000 Pa
| 1784684 | Specific Loss | - | 0.99762 | 30.000 Pa
| 1784692 | Coefficient from ASHRAE Table | SD4-1 | 0 | 0.000 Pa
85 | 1784663 | Coefficient from ASHRAE Table | - | 0 | 0.000 Pa | 0.000 Pa
| 1784668 | Coefficient from ASHRAE Table | SD4-2 | 0 | 0.000 Pa
86 | 1784650 | Coefficient from ASHRAE Table | SR3-1 | 1.15 | 4.214 Pa | 5.838 Pa
| 1784663 | Coefficient from ASHRAE Table | - | 0 | 0.000 Pa
| 2158600 | Coefficient from ASHRAE Table | SR5-11 | 0.44322 | 1.624 Pa
87 | 461495 | Specific Loss | - | 130.6948 | 150.000 Pa | 188.779 Pa
| 461501 | Specific Loss | - | 0.69704 | 0.800 Pa
| 461504 | Specific Loss | - | 0.69704 | 0.800 Pa
| 1268689 | Specific Loss | - | 26.139 | 30.000 Pa
| 2174089 | Coefficient from ASHRAE Table | SR5-11 | 6.2548 | 7.179 Pa
88 | 1621084 | Specific Loss | - | 11.6173 | 30.000 Pa | 190.835 Pa
| 1621086 | Specific Loss | - | 0.30979 | 0.800 Pa
| 1621088 | Specific Loss | - | 0.30979 | 0.800 Pa
| 1621090 | Specific Loss | - | 0.30979 | 0.800 Pa
| 1621094 | Specific Loss | - | 58.0866 | 150.000 Pa
| 2305420 | Coefficient from ASHRAE Table | SR5-11 | 3.2662 | 8.435 Pa
89 | 2305420 | Coefficient from ASHRAE Table | SR5-11 | 0 | 0.000 Pa | 1.797 Pa
| 2305308 | Coefficient from ASHRAE Table | SR5-11 | 0.3477 | 1.797 Pa
90 | 2305308 | Coefficient from ASHRAE Table | SR5-11 | 0 | 0.000 Pa | 0.000 Pa
| 1577092 | Coefficient from ASHRAE Table | - | 0 | 0.000 Pa
91 | 1562729 | Coefficient from ASHRAE Table | SR3-1 | 1.15 | 13.846 Pa | 39.636 Pa
| 1562749 | Coefficient from ASHRAE Table | CR3-1 | 0.11469 | 1.381 Pa
| 1562751 | Coefficient from ASHRAE Table | CR3-17 | 0.81615 | 9.826 Pa
| 1564697 | Coefficient from ASHRAE Table | SR3-1 | 1.15 | 13.846 Pa
| 1577092 | Coefficient from ASHRAE Table | - | 0 | 0.000 Pa
| 1621072 | Coefficient from ASHRAE Table | SR4-2 | 0.06125 | 0.737 Pa
92 | 1621072 | Coefficient from ASHRAE Table | SR4-2 | 0 | 0.000 Pa | 1.002 Pa
| 2305159 | Coefficient from ASHRAE Table | SR5-11 | 0.26293 | 1.002 Pa
93 | 461447 | Specific Loss | - | 130.6948 | 150.000 Pa | 181.600 Pa
| 461457 | Specific Loss | - | 0.69704 | 0.800 Pa
| 461459 | Specific Loss | - | 0.69704 | 0.800 Pa
| 461461 | Coefficient from ASHRAE Table | - | 0 | 0.000 Pa
| 1268742 | Specific Loss | - | 26.139 | 30.000 Pa
| 2174425 | Coefficient from ASHRAE Table | - | 0 | 0.000 Pa
94 | 2174425 | Coefficient from ASHRAE Table | - | 0 | 0.000 Pa | 0.371 Pa
| 2174388 | Coefficient from ASHRAE Table | SR5-11 | 0.32 | 0.371 Pa
95 | 2174388 | Coefficient from ASHRAE Table | SR5-11 | 0 | 0.000 Pa | 0.470 Pa
| 2174264 | Coefficient from ASHRAE Table | SR5-11 | 0.18 | 0.470 Pa
96 | 461467 | Coefficient from ASHRAE Table | - | 0 | 0.000 Pa | 184.104 Pa
| 461470 | Specific Loss | - | 130.6948 | 150.000 Pa
| 461474 | Specific Loss | - | 0.69704 | 0.800 Pa
| 1268719 | Specific Loss | - | 26.139 | 30.000 Pa
| 2174335 | Coefficient from ASHRAE Table | CD3-11 | 0.078005 | 0.090 Pa
| 2174388 | Coefficient from ASHRAE Table | SR5-11 | 2.8009 | 3.215 Pa
97 | 390937 | Coefficient from ASHRAE Table | SD5-24 | 12.5321 | 32.362 Pa | 34.762 Pa
| 1269120 | Specific Loss | - | 0.30979 | 0.800 Pa
| 1269124 | Specific Loss | - | 0.30979 | 0.800 Pa
| 1269141 | Specific Loss | - | 0.30979 | 0.800 Pa
98 | 461546 | Specific Loss | - | 0.30979 | 0.800 Pa | 185.873 Pa
| 461549 | Specific Loss | - | 11.6173 | 30.000 Pa
| 461552 | Coefficient from ASHRAE Table | CD3-11 | 0 | 0.000 Pa
| 461555 | Specific Loss | - | 58.0866 | 150.000 Pa
| 962964 | Specific Loss | - | 0.30979 | 0.800 Pa
| 2173897 | Coefficient from ASHRAE Table | SR5-11 | 1.6546 | 4.273 Pa
99 | 1784748 | Coefficient from ASHRAE Table | SD5-18 | 2.9 | 3.490 Pa | 3.490 Pa
100 | 1784745 | Specific Loss | - | 0.16619 | 0.800 Pa | 72.018 Pa
| 1784748 | Coefficient from ASHRAE Table | SD5-18 | 0 | 0.000 Pa
| 1784758 | Coefficient from ASHRAE Table | CD6-4 | 0.24 | 1.155 Pa
| 1784759 | Specific Loss | - | 6.232 | 30.000 Pa
| 1784821 | Coefficient from ASHRAE Table | SD5-24 | 8.3224 | 40.063 Pa
101 | 1562598 | Coefficient from ASHRAE Table | SD5-24 | 9.4767 | 12.970 Pa | 12.970 Pa
| 1562600 | Coefficient from ASHRAE Table | - | 0 | 0.000 Pa
102 | 1562598 | Coefficient from ASHRAE Table | SD5-24 | 0 | 0.000 Pa | 9.072 Pa
| 1562608 | Specific Loss | - | 0.064949 | 0.800 Pa
| 1562627 | Coefficient from ASHRAE Table | SD4-1 | 0.67158 | 8.272 Pa
103 | 1562627 | Coefficient from ASHRAE Table | SD4-1 | 0 | 0.000 Pa | 181.083 Pa
| 1562629 | Coefficient from ASHRAE Table | - | 0 | 0.000 Pa
| 1562631 | Specific Loss | - | 0.99762 | 30.000 Pa
| 1562632 | Specific Loss | - | 4.9881 | 150.000 Pa
| 1562633 | Coefficient from ASHRAE Table | SD4-1 | 0.036 | 1.083 Pa
104 | 1562633 | Coefficient from ASHRAE Table | SD4-1 | 0 | 0.000 Pa | 3.104 Pa
| 1562656 | Specific Loss | - | 0.064949 | 0.800 Pa
| 1562661 | Specific Loss | - | 0.064949 | 0.800 Pa
| 1562663 | Specific Loss | - | 0.064949 | 0.800 Pa
| 1562667 | Coefficient from ASHRAE Table | SD4-2 | 0.05713 | 0.704 Pa
105 | 1562667 | Coefficient from ASHRAE Table | SD4-2 | 0 | 0.000 Pa | 0.000 Pa
106 | 1607334 | Specific Loss | - | 130.6948 | 150.000 Pa | 182.400 Pa
| 1607335 | Specific Loss | - | 26.139 | 30.000 Pa
| 1607353 | Specific Loss | - | 0.69704 | 0.800 Pa
| 1607355 | Specific Loss | - | 0.69704 | 0.800 Pa
| 1607364 | Specific Loss | - | 0.69704 | 0.800 Pa
| 1617938 | Coefficient from ASHRAE Table | - | 0 | 0.000 Pa
107 | 1617938 | Coefficient from ASHRAE Table | - | 0 | 0.000 Pa | 0.287 Pa
| 2305722 | Coefficient from ASHRAE Table | SR5-11 | 0.99 | 0.287 Pa
108 | 2305722 | Coefficient from ASHRAE Table | SR5-11 | 0 | 0.000 Pa | 0.371 Pa
| 2305576 | Coefficient from ASHRAE Table | SR5-11 | 0.32 | 0.371 Pa
109 | 2305576 | Coefficient from ASHRAE Table | SR5-11 | 0 | 0.000 Pa | 0.470 Pa
| 2305538 | Coefficient from ASHRAE Table | SR5-11 | 0.18 | 0.470 Pa
110 | 2305538 | Coefficient from ASHRAE Table | SR5-11 | 0 | 0.000 Pa | 0.000 Pa
| 2305499 | Coefficient from ASHRAE Table | - | 0 | 0.000 Pa
111 | 2305499 | Coefficient from ASHRAE Table | - | 0 | 0.000 Pa | 0.000 Pa
| 1621074 | Coefficient from ASHRAE Table | - | 0 | 0.000 Pa
112 | 1621074 | Coefficient from ASHRAE Table | - | 0 | 0.000 Pa | 8.337 Pa
| 1621079 | Coefficient from ASHRAE Table | SR3-1 | 1.15 | 8.337 Pa
| 1621123 | Coefficient from ASHRAE Table | - | 0 | 0.000 Pa
113 | 1621120 | Coefficient from ASHRAE Table | - | 0 | 0.000 Pa | 30.000 Pa
| 1621123 | Coefficient from ASHRAE Table | - | 0 | 0.000 Pa
| 1621129 | Coefficient from ASHRAE Table | CR6-3 | 10.103 | 30.000 Pa
114 | 1621116 | Coefficient from ASHRAE Table | CR6-3 | 0 | 0.000 Pa | 58.088 Pa
| 1621120 | Coefficient from ASHRAE Table | - | 0 | 0.000 Pa
| 1621131 | Coefficient from ASHRAE Table | SR3-1 | 1.15 | 8.337 Pa
| 1621137 | Coefficient from ASHRAE Table | SR3-1 | 1.15 | 8.337 Pa
| 1632843 | Coefficient from ASHRAE Table | SR3-1 | 1.15 | 8.337 Pa
| 1632868 | Coefficient from ASHRAE Table | SR3-1 | 1.15 | 8.337 Pa
| 1632874 | Coefficient from ASHRAE Table | SR3-1 | 1.15 | 8.337 Pa
| 2305308 | Coefficient from ASHRAE Table | SR5-11 | 2.2627 | 16.403 Pa
115 | 1722367 | Specific Loss | - | 0.66475 | 0.800 Pa | 39.897 Pa
| 1722370 | Coefficient from ASHRAE Table | - | 0 | 0.000 Pa
| 1722375 | Specific Loss | - | 0.66475 | 0.800 Pa
| 1722378 | Specific Loss | - | 0.66475 | 0.800 Pa
| 1722381 | Specific Loss | - | 0.66475 | 0.800 Pa
| 1722384 | Coefficient from ASHRAE Table | - | 0 | 0.000 Pa
| 1722388 | Coefficient from ASHRAE Table | - | 0 | 0.000 Pa
| 1722393 | Specific Loss | - | 0.66475 | 0.800 Pa
| 1722396 | Specific Loss | - | 24.928 | 30.000 Pa
| 1722397 | Coefficient from ASHRAE Table | CD6-4 | 0.24 | 0.289 Pa
| 1722399 | Specific Loss | - | 0.66475 | 0.800 Pa
| 2291394 | Coefficient from ASHRAE Table | SD5-24 | 3.995 | 4.808 Pa
116 | 1722405 | Specific Loss | - | 0.25967 | 0.800 Pa | 30.572 Pa
| 1722407 | Specific Loss | - | 0.25967 | 0.800 Pa
| 2157848 | Coefficient from ASHRAE Table | SR5-11 | 2.5875 | 7.972 Pa
| 2157867 | Coefficient from ASHRAE Table | CD3-11 | 0 | 0.000 Pa
| 2291394 | Coefficient from ASHRAE Table | SD5-24 | 6.8163 | 21.000 Pa
117 | 1514010 | Specific Loss | - | 0.17426 | 0.800 Pa | 2.496 Pa
| 1514013 | Specific Loss | - | 0.17426 | 0.800 Pa
| 1514016 | Specific Loss | - | 0.17426 | 0.800 Pa
| 1514022 | Coefficient from ASHRAE Table | - | 0 | 0.000 Pa
| 1514051 | Coefficient from ASHRAE Table | SD4-1 | 0.020988 | 0.096 Pa
118 | 1514042 | Coefficient from ASHRAE Table | SD5-24 | 4.4 | 12.611 Pa | 12.611 Pa
| 1514051 | Coefficient from ASHRAE Table | SD4-1 | 0 | 0.000 Pa
119 | 1722411 | Specific Loss | - | 58.0866 | 150.000 Pa | 191.268 Pa
| 1722412 | Specific Loss | - | 11.6173 | 30.000 Pa
| 1722413 | Specific Loss | - | 0.30979 | 0.800 Pa
| 2291394 | Coefficient from ASHRAE Table | SD5-24 | 4.0536 | 10.468 Pa
120 | 1803448 | Specific Loss | - | 0.30979 | 0.800 Pa | 193.250 Pa
| 1803451 | Specific Loss | - | 0.30979 | 0.800 Pa
| 1803453 | Specific Loss | - | 0.30979 | 0.800 Pa
| 1803468 | Specific Loss | - | 11.6173 | 30.000 Pa
| 1803469 | Specific Loss | - | 58.0866 | 150.000 Pa
| 2159643 | Coefficient from ASHRAE Table | SR5-11 | 4.2014 | 10.850 Pa
| 2159696 | Coefficient from ASHRAE Table | CD3-11 | 0 | 0.000 Pa
121 | 1803437 | Specific Loss | - | 0.30979 | 0.800 Pa | 192.331 Pa
| 1803440 | Specific Loss | - | 0.30979 | 0.800 Pa
| 1803442 | Specific Loss | - | 0.30979 | 0.800 Pa
| 1803466 | Specific Loss | - | 11.6173 | 30.000 Pa
| 1803467 | Specific Loss | - | 58.0866 | 150.000 Pa
| 2159757 | Coefficient from ASHRAE Table | SR5-11 | 3.5359 | 9.131 Pa
| 2159759 | Specific Loss | - | 0.30979 | 0.800 Pa
122 | 1722073 | Specific Loss | - | 0.58454 | 0.800 Pa | 29.422 Pa
| 1722075 | Specific Loss | - | 0.58454 | 0.800 Pa
| 1722085 | Specific Loss | - | 0.58454 | 0.800 Pa
| 2289588 | Coefficient from ASHRAE Table | SD5-24 | 19.7443 | 27.022 Pa
123 | 2289588 | Coefficient from ASHRAE Table | SD5-24 | 0 | 0.000 Pa | 0.748 Pa
| 2292088 | Coefficient from ASHRAE Table | SD5-10 | 0.13667 | 0.748 Pa
124 | 1784957 | Specific Loss | - | 0.69704 | 0.800 Pa | 200.562 Pa
| 1784959 | Specific Loss | - | 0.69704 | 0.800 Pa
| 1784961 | Specific Loss | - | 0.69704 | 0.800 Pa
| 1784963 | Specific Loss | - | 26.139 | 30.000 Pa
| 1784964 | Specific Loss | - | 130.6948 | 150.000 Pa
| 1784967 | Specific Loss | - | 0.69704 | 0.800 Pa
| 1784969 | Coefficient from ASHRAE Table | - | 0 | 0.000 Pa
| 1784971 | Coefficient from ASHRAE Table | SD5-24 | 15.1276 | 17.362 Pa
125 | 1722661 | Specific Loss | - | 0.69704 | 0.800 Pa | 184.815 Pa
| 1734146 | Specific Loss | - | 0.69704 | 0.800 Pa
| 1734148 | Specific Loss | - | 26.139 | 30.000 Pa
| 1734149 | Specific Loss | - | 130.6948 | 150.000 Pa
| 1734187 | Coefficient from ASHRAE Table | - | 0 | 0.000 Pa
| 2158819 | Coefficient from ASHRAE Table | SR5-11 | 2.8009 | 3.215 Pa
126 | 1784903 | Specific Loss | - | 0.30979 | 0.800 Pa | 196.111 Pa
| 1784905 | Specific Loss | - | 0.30979 | 0.800 Pa
| 1784907 | Specific Loss | - | 0.30979 | 0.800 Pa
| 1784909 | Specific Loss | - | 11.6173 | 30.000 Pa
| 1784910 | Specific Loss | - | 58.0866 | 150.000 Pa
| 2290758 | Coefficient from ASHRAE Table | SD5-24 | 4.9997 | 12.911 Pa
| 2290770 | Specific Loss | - | 0.30979 | 0.800 Pa
127 | 1784748 | Coefficient from ASHRAE Table | SD5-18 | 20.3496 | 24.490 Pa | 24.490 Pa
128 | 1562576 | Coefficient from ASHRAE Table | SD5-24 | 4.4 | 6.022 Pa | 6.022 Pa
| 1562579 | Coefficient from ASHRAE Table | - | 0 | 0.000 Pa
129 | 1562576 | Coefficient from ASHRAE Table | SD5-24 | 0 | 0.000 Pa | 42.733 Pa
| 1562598 | Coefficient from ASHRAE Table | SD5-24 | 7.8061 | 42.733 Pa
130 | 1562553 | Specific Loss | - | 0.58454 | 0.800 Pa | 27.822 Pa
| 1562556 | Coefficient from ASHRAE Table | - | 0 | 0.000 Pa
| 1562559 | Coefficient from ASHRAE Table | - | 0 | 0.000 Pa
| 1562562 | Coefficient from ASHRAE Table | - | 0 | 0.000 Pa
| 1562576 | Coefficient from ASHRAE Table | SD5-24 | 19.7443 | 27.022 Pa
131 | 1514116 | Specific Loss | - | 0.25967 | 0.800 Pa | 50.695 Pa
| 1514216 | Specific Loss | - | 9.7375 | 30.000 Pa
| 1514282 | Coefficient from ASHRAE Table | CD6-4 | 0.24 | 0.739 Pa
| 1514328 | Specific Loss | - | 0.25967 | 0.800 Pa
| 1514331 | Specific Loss | - | 0.25967 | 0.800 Pa
| 1722149 | Specific Loss | - | 0.25967 | 0.800 Pa
| 1722155 | Specific Loss | - | 0.25967 | 0.800 Pa
| 1722158 | Specific Loss | - | 0.25967 | 0.800 Pa
| 1722160 | Coefficient from ASHRAE Table | - | 0 | 0.000 Pa
| 1722188 | Coefficient from ASHRAE Table | SD5-24 | 4.4 | 13.556 Pa
| 1722203 | Specific Loss | - | 0.25967 | 0.800 Pa
| 1722205 | Specific Loss | - | 0.25967 | 0.800 Pa
| 1722207 | Coefficient from ASHRAE Table | - | 0 | 0.000 Pa
132 | 1722099 | Specific Loss | - | 0.58454 | 0.800 Pa | 7.622 Pa
| 2289588 | Coefficient from ASHRAE Table | SD5-24 | 4.4 | 6.022 Pa
| 2289594 | Specific Loss | - | 0.58454 | 0.800 Pa
133 | 1681109 | Coefficient from ASHRAE Table | SD5-24 | 4.4 | 7.891 Pa | 8.691 Pa
| 1684553 | Specific Loss | - | 0.4461 | 0.800 Pa
134 | 1681109 | Coefficient from ASHRAE Table | SD5-24 | 0 | 0.000 Pa | 183.550 Pa
| 1684559 | Specific Loss | - | 0.11153 | 0.800 Pa
| 1684562 | Specific Loss | - | 0.11153 | 0.800 Pa
| 1684565 | Specific Loss | - | 0.11153 | 0.800 Pa
| 1684568 | Specific Loss | - | 4.1822 | 30.000 Pa
| 1684569 | Specific Loss | - | 20.9112 | 150.000 Pa
| 1684570 | Specific Loss | - | 0.11153 | 0.800 Pa
| 1684573 | Coefficient from ASHRAE Table | - | 0 | 0.000 Pa
| 1684592 | Coefficient from ASHRAE Table | SD4-1 | 0.048724 | 0.350 Pa
135 | 1684586 | Coefficient from ASHRAE Table | SD5-24 | 3.9529 | 4.757 Pa | 4.757 Pa
| 1684592 | Coefficient from ASHRAE Table | SD4-1 | 0 | 0.000 Pa
| 1684596 | Coefficient from ASHRAE Table | - | 0 | 0.000 Pa
136 | 1684586 | Coefficient from ASHRAE Table | SD5-24 | 8.9029 | 21.000 Pa | 30.317 Pa
| 1684601 | Coefficient from ASHRAE Table | SD5-24 | 3.95 | 9.317 Pa
137 | 1684601 | Coefficient from ASHRAE Table | SD5-24 | 4.3624 | 21.000 Pa | 40.063 Pa
| 1684624 | Coefficient from ASHRAE Table | SD5-24 | 3.96 | 19.063 Pa
138 | 1684624 | Coefficient from ASHRAE Table | SD5-24 | 3.0295 | 21.000 Pa | 69.520 Pa
| 1684665 | Coefficient from ASHRAE Table | SD5-24 | 6.9995 | 48.520 Pa
139 | 1684665 | Coefficient from ASHRAE Table | SD5-24 | 0 | 0.000 Pa | 0.220 Pa
| 1684687 | Coefficient from ASHRAE Table | SD4-1 | 0.020281 | 0.220 Pa
140 | 1684678 | Coefficient from ASHRAE Table | SD5-24 | 3.96 | 27.258 Pa | 27.258 Pa
| 1684683 | Coefficient from ASHRAE Table | - | 0 | 0.000 Pa
| 1684687 | Coefficient from ASHRAE Table | SD4-1 | 0 | 0.000 Pa
141 | 1684678 | Coefficient from ASHRAE Table | SD5-24 | 2.1186 | 21.000 Pa | 23.963 Pa
| 1684713 | Specific Loss | - | 0.080709 | 0.800 Pa
| 1684716 | Specific Loss | - | 0.080709 | 0.800 Pa
| 1684722 | Specific Loss | - | 0.080709 | 0.800 Pa
| 1684727 | Coefficient from ASHRAE Table | - | 0 | 0.000 Pa
| 1684751 | Coefficient from ASHRAE Table | SD4-2 | 0.05683 | 0.563 Pa
142 | 2173268 | Coefficient from ASHRAE Table | SR5-11 | 1.74 | 2.554 Pa | 2.554 Pa
| 1684751 | Coefficient from ASHRAE Table | SD4-2 | 0 | 0.000 Pa
143 | 2173268 | Coefficient from ASHRAE Table | SR5-11 | 0 | 0.000 Pa | 18.383 Pa
| 1744360 | Coefficient from ASHRAE Table | SR3-1 | 1.15 | 9.192 Pa
| 1835998 | Coefficient from ASHRAE Table | - | 0 | 0.000 Pa
| 1836008 | Coefficient from ASHRAE Table | SR3-1 | 1.15 | 9.192 Pa
| 1836012 | Coefficient from ASHRAE Table | CR6-3 | 0 | 0.000 Pa
| 1836035 | Coefficient from ASHRAE Table | CR6-3 | 0 | 0.000 Pa
144 | 1835998 | Coefficient from ASHRAE Table | - | 0 | 0.000 Pa | 0.318 Pa
| 2173125 | Coefficient from ASHRAE Table | SR5-11 | 0.06383 | 0.318 Pa
145 | 2173125 | Coefficient from ASHRAE Table | SR5-11 | 0 | 0.000 Pa | 18.749 Pa
| 2173091 | Coefficient from ASHRAE Table | SR3-1 | 1.15 | 7.186 Pa
| 2173094 | Coefficient from ASHRAE Table | SR5-11 | 1.8505 | 11.563 Pa
146 | 2173094 | Coefficient from ASHRAE Table | SR5-11 | 0 | 0.000 Pa | 0.300 Pa
| 1831106 | Coefficient from ASHRAE Table | SR4-2 | 0.037143 | 0.300 Pa
147 | 1831106 | Coefficient from ASHRAE Table | SR4-2 | 0 | 0.000 Pa | 1.562 Pa
| 2159178 | Coefficient from ASHRAE Table | SR5-11 | 0.35836 | 1.562 Pa
148 | 1775896 | Specific Loss | - | 0.2276 | 0.800 Pa | 17.865 Pa
| 2479568 | Specific Loss | - | 0.2276 | 0.800 Pa
| 2479570 | Specific Loss | - | 0.2276 | 0.800 Pa
| 2479825 | Coefficient from ASHRAE Table | SD5-24 | 4.4 | 15.465 Pa
149 | 1713991 | Specific Loss | - | 0.056901 | 0.800 Pa | 204.072 Pa
| 1748170 | Specific Loss | - | 0.056901 | 0.800 Pa
| 1748762 | Coefficient from ASHRAE Table | SD4-1 | 0.04781 | 0.672 Pa
| 1748816 | Coefficient from ASHRAE Table | - | 0 | 0.000 Pa
| 1749251 | Coefficient from ASHRAE Table | - | 0 | 0.000 Pa
| 1763104 | Specific Loss | - | 2.1338 | 30.000 Pa
| 1763108 | Specific Loss | - | 10.669 | 150.000 Pa
| 2479816 | Specific Loss | - | 0.056901 | 0.800 Pa
| 2479825 | Coefficient from ASHRAE Table | SD5-24 | 1.4937 | 21.000 Pa
150 | 1748525 | Coefficient from ASHRAE Table | SD5-24 | 7.7995 | 11.692 Pa | 11.692 Pa
| 1748727 | Coefficient from ASHRAE Table | - | 0 | 0.000 Pa
| 1748762 | Coefficient from ASHRAE Table | SD4-1 | 0 | 0.000 Pa
151 | 1713967 | Specific Loss | - | 0.072437 | 0.800 Pa | 92.767 Pa
| 1713969 | Specific Loss | - | 0.072437 | 0.800 Pa
| 1713973 | Specific Loss | - | 0.072437 | 0.800 Pa
| 1713976 | Specific Loss | - | 0.072437 | 0.800 Pa
| 1714027 | Specific Loss | - | 0.072437 | 0.800 Pa
| 1747552 | Specific Loss | - | 0.072437 | 0.800 Pa
| 1747802 | Specific Loss | - | 0.072437 | 0.800 Pa
| 1747910 | Specific Loss | - | 0.072437 | 0.800 Pa
| 1747985 | Coefficient from ASHRAE Table | - | 0 | 0.000 Pa
| 1748048 | Coefficient from ASHRAE Table | - | 0 | 0.000 Pa
| 1748093 | Specific Loss | - | 0.072437 | 0.800 Pa
| 1748525 | Coefficient from ASHRAE Table | SD5-24 | 1.9015 | 21.000 Pa
| 1775847 | Coefficient from ASHRAE Table | SD5-24 | 5.8464 | 64.567 Pa
152 | 1713943 | Specific Loss | - | 0.056571 | 0.800 Pa | 58.935 Pa
| 1713945 | Specific Loss | - | 0.056571 | 0.800 Pa
| 1713955 | Specific Loss | - | 0.056571 | 0.800 Pa
| 1751079 | Specific Loss | - | 0.056571 | 0.800 Pa
| 1751088 | Coefficient from ASHRAE Table | SD5-24 | 3.9413 | 55.735 Pa
| 1751106 | Coefficient from ASHRAE Table | - | 0 | 0.000 Pa
| 1775847 | Coefficient from ASHRAE Table | SD5-24 | 0 | 0.000 Pa
153 | 1746731 | Specific Loss | - | 0.045399 | 0.800 Pa | 42.294 Pa
| 1751088 | Coefficient from ASHRAE Table | SD5-24 | 1.1917 | 21.000 Pa
| 2173268 | Coefficient from ASHRAE Table | SR5-11 | 1.1176 | 19.694 Pa
| 2173284 | Specific Loss | - | 0.045399 | 0.800 Pa
| 2173290 | Coefficient from ASHRAE Table | CD3-11 | 0 | 0.000 Pa
154 | 1763089 | Coefficient from ASHRAE Table | SD4-1 | 0.036 | 0.152 Pa | 0.152 Pa
155 | 1763083 | Coefficient from ASHRAE Table | SD5-18 | 15.0178 | 26.026 Pa | 26.026 Pa
| 1763085 | Coefficient from ASHRAE Table | - | 0 | 0.000 Pa
| 1763089 | Coefficient from ASHRAE Table | SD4-1 | 0 | 0.000 Pa
156 | 1748270 | Specific Loss | - | 0.11541 | 0.800 Pa | 56.674 Pa
| 1748303 | Specific Loss | - | 0.11541 | 0.800 Pa
| 1748336 | Specific Loss | - | 4.3278 | 30.000 Pa
| 1748368 | Coefficient from ASHRAE Table | CD6-4 | 0.24 | 1.664 Pa
| 1748447 | Coefficient from ASHRAE Table | - | 0 | 0.000 Pa
| 1748525 | Coefficient from ASHRAE Table | SD5-24 | 3.3771 | 23.410 Pa
| 1763083 | Coefficient from ASHRAE Table | SD5-18 | 0 | 0.000 Pa
157 | 982808 | Specific Loss | - | 0.4461 | 0.800 Pa | 9.491 Pa
| 982812 | Specific Loss | - | 0.4461 | 0.800 Pa
| 982823 | Coefficient from ASHRAE Table | SD5-24 | 4.4 | 7.891 Pa
158 | 982823 | Coefficient from ASHRAE Table | SD5-24 | 2.9276 | 21.000 Pa | 231.115 Pa
| 982830 | Specific Loss | - | 0.11153 | 0.800 Pa
| 1589729 | Coefficient from ASHRAE Table | SD5-24 | 4.0867 | 29.315 Pa
| 1589738 | Specific Loss | - | 20.9112 | 150.000 Pa
| 1589739 | Specific Loss | - | 4.1822 | 30.000 Pa
159 | 1589729 | Coefficient from ASHRAE Table | SD5-24 | 0 | 0.000 Pa | 2.966 Pa
| 1589740 | Specific Loss | - | 0.090484 | 0.800 Pa
| 1589743 | Specific Loss | - | 0.090484 | 0.800 Pa
| 1589745 | Specific Loss | - | 0.090484 | 0.800 Pa
| 1590103 | Coefficient from ASHRAE Table | SD4-2 | 0.063984 | 0.566 Pa
160 | 2648090 | Coefficient from ASHRAE Table | SR5-11 | 3.2408 | 7.544 Pa | 10.291 Pa
| 1590099 | Coefficient from ASHRAE Table | SR3-1 | 1.18 | 2.747 Pa
| 1590103 | Coefficient from ASHRAE Table | SD4-2 | 0 | 0.000 Pa
161 | 2648090 | Coefficient from ASHRAE Table | SR5-11 | 0 | 0.000 Pa | 37.961 Pa
| 1590093 | Coefficient from ASHRAE Table | SR3-1 | 1.18 | 21.900 Pa
| 1590122 | Coefficient from ASHRAE Table | CR3-17 | 0.42022 | 7.799 Pa
| 1590123 | Coefficient from ASHRAE Table | CR3-17 | 0.42022 | 7.799 Pa
| 2104907 | Coefficient from ASHRAE Table | SR4-1 | 0.025 | 0.464 Pa
162 | 1667851 | Coefficient from ASHRAE Table | CR6-3 | 0 | 0.000 Pa | 2.028 Pa
| 1667852 | Coefficient from ASHRAE Table | CR6-3 | 0 | 0.000 Pa
| 2104907 | Coefficient from ASHRAE Table | SR4-1 | 0 | 0.000 Pa
| 2104910 | Coefficient from ASHRAE Table | SR4-1 | 0.19426 | 2.028 Pa
163 | 1714175 | Coefficient from ASHRAE Table | SR4-1 | 0.025 | 0.464 Pa | 0.464 Pa
| 2104910 | Coefficient from ASHRAE Table | SR4-1 | 0 | 0.000 Pa
164 | 1606961 | Coefficient from ASHRAE Table | SR3-1 | 1.15 | 12.005 Pa | 24.553 Pa
| 1606962 | Coefficient from ASHRAE Table | SR3-1 | 1.15 | 12.005 Pa
| 1714175 | Coefficient from ASHRAE Table | SR4-1 | 0 | 0.000 Pa
| 1829345 | Coefficient from ASHRAE Table | SR4-2 | 0.051931 | 0.542 Pa
165 | 1829345 | Coefficient from ASHRAE Table | SR4-2 | 0 | 0.000 Pa | 1.986 Pa
| 2173094 | Coefficient from ASHRAE Table | SR5-11 | 0.96316 | 1.986 Pa
166 | 1684601 | Coefficient from ASHRAE Table | SD5-24 | 3.337 | 8.617 Pa | 191.817 Pa
| 1684604 | Coefficient from ASHRAE Table | - | 0 | 0.000 Pa
| 1684607 | Specific Loss | - | 0.30979 | 0.800 Pa
| 1684609 | Specific Loss | - | 0.30979 | 0.800 Pa
| 1684612 | Specific Loss | - | 0.30979 | 0.800 Pa
| 1684615 | Specific Loss | - | 11.6173 | 30.000 Pa
| 1684616 | Specific Loss | - | 58.0866 | 150.000 Pa
| 1684618 | Coefficient from ASHRAE Table | - | 0 | 0.000 Pa
| 1684621 | Specific Loss | - | 0.30979 | 0.800 Pa
167 | 1684624 | Coefficient from ASHRAE Table | SD5-24 | 9.0991 | 10.443 Pa | 193.643 Pa
| 1684627 | Coefficient from ASHRAE Table | - | 0 | 0.000 Pa
| 1684630 | Specific Loss | - | 0.69704 | 0.800 Pa
| 1684633 | Specific Loss | - | 0.69704 | 0.800 Pa
| 1684636 | Specific Loss | - | 0.69704 | 0.800 Pa
| 1684645 | Specific Loss | - | 26.139 | 30.000 Pa
| 1684646 | Specific Loss | - | 130.6948 | 150.000 Pa
| 1684647 | Specific Loss | - | 0.69704 | 0.800 Pa
168 | 1684651 | Specific Loss | - | 0.30979 | 0.800 Pa | 196.111 Pa
| 1684653 | Specific Loss | - | 0.30979 | 0.800 Pa
| 1684658 | Specific Loss | - | 0.30979 | 0.800 Pa
| 1684660 | Specific Loss | - | 11.6173 | 30.000 Pa
| 1684661 | Specific Loss | - | 58.0866 | 150.000 Pa
| 1684665 | Coefficient from ASHRAE Table | SD5-24 | 4.9997 | 12.911 Pa
| 1684670 | Coefficient from ASHRAE Table | - | 0 | 0.000 Pa
| 1684674 | Specific Loss | - | 0.30979 | 0.800 Pa
169 | 1680691 | Specific Loss | - | 0.27228 | 0.800 Pa | 344.067 Pa
| 1742972 | Specific Loss | - | 0.27228 | 0.800 Pa
| 1742975 | Specific Loss | - | 0.27228 | 0.800 Pa
| 1742979 | Coefficient from ASHRAE Table | CD6-4 | 51.2926 | 150.705 Pa
| 1742981 | Specific Loss | - | 0.27228 | 0.800 Pa
| 1742983 | Specific Loss | - | 0.27228 | 0.800 Pa
| 1742988 | Coefficient from ASHRAE Table | - | 0 | 0.000 Pa
| 1746867 | Specific Loss | - | 10.2105 | 30.000 Pa
| 1746868 | Specific Loss | - | 51.0526 | 150.000 Pa
| 1822521 | Specific Loss | - | 0.27228 | 0.800 Pa
| 2173125 | Coefficient from ASHRAE Table | SR5-11 | 2.9141 | 8.562 Pa
170 | 2479825 | Coefficient from ASHRAE Table | SD5-24 | 4.4 | 15.465 Pa | 15.465 Pa
171 | 982814 | Specific Loss | - | 0.4461 | 0.800 Pa | 8.691 Pa
| 982823 | Coefficient from ASHRAE Table | SD5-24 | 4.4 | 7.891 Pa
172 | 1833844 | Specific Loss | - | 0.27228 | 0.800 Pa | 344.772 Pa
| 1834629 | Specific Loss | - | 0.27228 | 0.800 Pa
| 1834631 | Specific Loss | - | 0.27228 | 0.800 Pa
| 1834635 | Specific Loss | - | 51.0526 | 150.000 Pa
| 1834636 | Specific Loss | - | 10.2105 | 30.000 Pa
| 1834637 | Specific Loss | - | 0.27228 | 0.800 Pa
| 1835672 | Coefficient from ASHRAE Table | CD6-4 | 51.2926 | 150.705 Pa
| 1835755 | Specific Loss | - | 0.27228 | 0.800 Pa
| 1835760 | Coefficient from ASHRAE Table | - | 0 | 0.000 Pa
| 1835763 | Specific Loss | - | 0.27228 | 0.800 Pa
| 2159242 | Coefficient from ASHRAE Table | SR5-11 | 3.1538 | 9.266 Pa
173 | 982770 | Coefficient from ASHRAE Table | SD5-24 | 9.0991 | 10.443 Pa | 192.843 Pa
| 982794 | Specific Loss | - | 0.69704 | 0.800 Pa
| 982797 | Specific Loss | - | 0.69704 | 0.800 Pa
| 982799 | Specific Loss | - | 0.69704 | 0.800 Pa
| 1015507 | Specific Loss | - | 130.6948 | 150.000 Pa
| 1015508 | Specific Loss | - | 26.139 | 30.000 Pa
174 | 982770 | Coefficient from ASHRAE Table | SD5-24 | 0 | 0.000 Pa | 0.141 Pa
| 1589735 | Coefficient from ASHRAE Table | SD4-1 | 0.020281 | 0.141 Pa
175 | 1589729 | Coefficient from ASHRAE Table | SD5-24 | 8.7181 | 38.406 Pa | 38.406 Pa
| 1589732 | Coefficient from ASHRAE Table | - | 0 | 0.000 Pa
| 1589735 | Coefficient from ASHRAE Table | SD4-1 | 0 | 0.000 Pa
176 | 1684678 | Coefficient from ASHRAE Table | SD5-24 | 6.3399 | 16.372 Pa | 199.572 Pa
| 1684693 | Specific Loss | - | 11.6173 | 30.000 Pa
| 1684699 | Specific Loss | - | 58.0866 | 150.000 Pa
| 1684705 | Coefficient from ASHRAE Table | - | 0 | 0.000 Pa
| 1684709 | Specific Loss | - | 0.30979 | 0.800 Pa
| 1684736 | Specific Loss | - | 0.30979 | 0.800 Pa
| 1684744 | Specific Loss | - | 0.30979 | 0.800 Pa
| 1684748 | Specific Loss | - | 0.30979 | 0.800 Pa
177 | 982722 | Coefficient from ASHRAE Table | SD5-24 | 3.337 | 8.617 Pa | 191.017 Pa
| 982749 | Specific Loss | - | 0.30979 | 0.800 Pa
| 982751 | Specific Loss | - | 0.30979 | 0.800 Pa
| 982753 | Specific Loss | - | 0.30979 | 0.800 Pa
| 1015504 | Specific Loss | - | 58.0866 | 150.000 Pa
| 1015505 | Specific Loss | - | 11.6173 | 30.000 Pa
178 | 982722 | Coefficient from ASHRAE Table | SD5-24 | 0 | 0.000 Pa | 191.218 Pa
| 982764 | Coefficient from ASHRAE Table | CD6-4 | 31.4001 | 151.155 Pa
| 982770 | Coefficient from ASHRAE Table | SD5-24 | 8.3224 | 40.063 Pa
179 | 1763091 | Coefficient from ASHRAE Table | SD4-1 | 0.036 | 0.152 Pa | 0.152 Pa
180 | 1763083 | Coefficient from ASHRAE Table | SD5-18 | 2.9 | 5.026 Pa | 5.026 Pa
| 1763087 | Coefficient from ASHRAE Table | - | 0 | 0.000 Pa
| 1763091 | Coefficient from ASHRAE Table | SD4-1 | 0 | 0.000 Pa
181 | 460651 | Specific Loss | - | 0.25967 | 0.800 Pa | 33.253 Pa
| 460654 | Specific Loss | - | 0.25967 | 0.800 Pa
| 460657 | Specific Loss | - | 0.25967 | 0.800 Pa
| 674007 | Coefficient from ASHRAE Table | SD4-1 | 0.037012 | 0.114 Pa
| 674032 | Coefficient from ASHRAE Table | CD6-4 | 0.24 | 0.739 Pa
| 674033 | Specific Loss | - | 9.7375 | 30.000 Pa
182 | 673981 | Not Defined | - | 0 | 0.000 Pa | 0.000 Pa
| 674007 | Coefficient from ASHRAE Table | SD4-1 | 0 | 0.000 Pa
| 674011 | Coefficient from ASHRAE Table | - | 0 | 0.000 Pa
183 | 673981 | Not Defined | - | 1.7593 | 21.000 Pa | 89.057 Pa
| 722542 | Coefficient from ASHRAE Table | SD5-24 | 5.7014 | 68.057 Pa
184 | 722542 | Coefficient from ASHRAE Table | SD5-24 | 0 | 0.000 Pa | 62.138 Pa
| 722566 | Specific Loss | - | 0.053427 | 0.800 Pa
| 722574 | Specific Loss | - | 0.053427 | 0.800 Pa
| 722577 | Specific Loss | - | 0.053427 | 0.800 Pa
| 722579 | Specific Loss | - | 0.053427 | 0.800 Pa
| 722596 | Coefficient from ASHRAE Table | SD5-24 | 3.9361 | 58.938 Pa
185 | 722586 | Specific Loss | - | 0.043587 | 0.800 Pa | 179.068 Pa
| 722590 | Specific Loss | - | 0.043587 | 0.800 Pa
| 722596 | Coefficient from ASHRAE Table | SD5-24 | 1.1442 | 21.000 Pa
| 763545 | Coefficient from ASHRAE Table | - | 0 | 0.000 Pa
| 763548 | Coefficient from ASHRAE Table | - | 0 | 0.000 Pa
| 763551 | Coefficient from ASHRAE Table | CD6-4 | 8.4125 | 154.405 Pa
| 790293 | Specific Loss | - | 0.043587 | 0.800 Pa
| 790296 | Specific Loss | - | 0.043587 | 0.800 Pa
| 2648091 | Specific Loss | - | 0.025249 | 0.463 Pa
| 2648117 | Coefficient from ASHRAE Table | - | 0 | 0.000 Pa
186 | 2648090 | Coefficient from ASHRAE Table | SR5-11 | 1.905 | 35.355 Pa | 35.355 Pa
| 2648091 | Specific Loss | - | 0 | 0.000 Pa
187 | 707141 | Specific Loss | - | 0.30979 | 0.800 Pa | 202.134 Pa
| 707150 | Specific Loss | - | 58.0866 | 150.000 Pa
| 707151 | Specific Loss | - | 11.6173 | 30.000 Pa
| 707165 | Specific Loss | - | 0.30979 | 0.800 Pa
| 707167 | Specific Loss | - | 0.30979 | 0.800 Pa
| 722542 | Coefficient from ASHRAE Table | SD5-24 | 7.3321 | 18.934 Pa
| 722545 | Specific Loss | - | 0.30979 | 0.800 Pa
188 | 656434 | Coefficient from ASHRAE Table | SD5-24 | 3.6205 | 20.849 Pa | 354.632 Pa
| 656445 | Specific Loss | - | 0.13892 | 0.800 Pa
| 656447 | Specific Loss | - | 0.13892 | 0.800 Pa
| 656451 | Specific Loss | - | 0.13892 | 0.800 Pa
| 656454 | Specific Loss | - | 26.0473 | 150.000 Pa
| 656455 | Specific Loss | - | 5.2095 | 30.000 Pa
| 763543 | Coefficient from ASHRAE Table | CD6-4 | 26.2873 | 151.382 Pa
189 | 656434 | Coefficient from ASHRAE Table | SD5-24 | 0 | 0.000 Pa | 3.200 Pa
| 656494 | Specific Loss | - | 0.057504 | 0.800 Pa
| 656496 | Specific Loss | - | 0.057504 | 0.800 Pa
| 656503 | Specific Loss | - | 0.057504 | 0.800 Pa
| 656505 | Specific Loss | - | 0.057504 | 0.800 Pa
| 673981 | Not Defined | - | 0 | 0.000 Pa
| 673984 | Coefficient from ASHRAE Table | - | 0 | 0.000 Pa
190 | 1713928 | Specific Loss | - | 0.4461 | 0.800 Pa | 202.292 Pa
| 1713934 | Specific Loss | - | 0.4461 | 0.800 Pa
| 1751430 | Specific Loss | - | 16.7289 | 30.000 Pa
| 1751468 | Specific Loss | - | 83.6446 | 150.000 Pa
| 1751552 | Specific Loss | - | 0.4461 | 0.800 Pa
| 1751609 | Coefficient from ASHRAE Table | - | 0 | 0.000 Pa
| 1751629 | Specific Loss | - | 0.4461 | 0.800 Pa
| 1775837 | Specific Loss | - | 0.4461 | 0.800 Pa
| 1775847 | Coefficient from ASHRAE Table | SD5-24 | 10.2002 | 18.292 Pa
191 | 845355 | Specific Loss | - | 0.4461 | 0.800 Pa | 29.691 Pa
| 845384 | Coefficient from ASHRAE Table | SD5-24 | 16.1103 | 28.891 Pa
192 | 845384 | Coefficient from ASHRAE Table | SD5-24 | 0 | 0.000 Pa | 181.950 Pa
| 893218 | Specific Loss | - | 0.11153 | 0.800 Pa
| 893223 | Specific Loss | - | 0.11153 | 0.800 Pa
| 893228 | Coefficient from ASHRAE Table | - | 0 | 0.000 Pa
| 893231 | Specific Loss | - | 20.9112 | 150.000 Pa
| 893234 | Specific Loss | - | 4.1822 | 30.000 Pa
| 893286 | Coefficient from ASHRAE Table | SD4-1 | 0.048724 | 0.350 Pa
193 | 893286 | Coefficient from ASHRAE Table | SD4-1 | 0 | 0.000 Pa | 25.757 Pa
| 893296 | Coefficient from ASHRAE Table | SD5-24 | 21.4025 | 25.757 Pa
| 893301 | Coefficient from ASHRAE Table | - | 0 | 0.000 Pa
194 | 893261 | Specific Loss | - | 0.33916 | 0.800 Pa | 33.517 Pa
| 893296 | Coefficient from ASHRAE Table | SD5-24 | 0 | 0.000 Pa
| 982692 | Specific Loss | - | 0.33916 | 0.800 Pa
| 982695 | Coefficient from ASHRAE Table | - | 0 | 0.000 Pa
| 982708 | Specific Loss | - | 0.33916 | 0.800 Pa
| 982713 | Specific Loss | - | 0.33916 | 0.800 Pa
| 982722 | Coefficient from ASHRAE Table | SD5-24 | 12.8529 | 30.317 Pa
| 982732 | Coefficient from ASHRAE Table | - | 0 | 0.000 Pa
195 | 1681109 | Coefficient from ASHRAE Table | SD5-24 | 16.1103 | 28.891 Pa | 30.491 Pa
| 1684556 | Specific Loss | - | 0.4461 | 0.800 Pa
| 2304648 | Specific Loss | - | 0.4461 | 0.800 Pa
196 | 845384 | Coefficient from ASHRAE Table | SD5-24 | 4.4 | 7.891 Pa | 7.891 Pa
197 | 893264 | Specific Loss | - | 0.69704 | 0.800 Pa | 186.503 Pa
| 893271 | Specific Loss | - | 0.69704 | 0.800 Pa
| 893273 | Specific Loss | - | 0.69704 | 0.800 Pa
| 893296 | Coefficient from ASHRAE Table | SD5-24 | 3.5746 | 4.103 Pa
| 1015501 | Specific Loss | - | 130.6948 | 150.000 Pa
| 1015502 | Specific Loss | - | 26.139 | 30.000 Pa
198 | 1681098 | Specific Loss | - | 0.69704 | 0.800 Pa | 187.303 Pa
| 1681101 | Specific Loss | - | 0.69704 | 0.800 Pa
| 1681103 | Specific Loss | - | 0.69704 | 0.800 Pa
| 1684576 | Specific Loss | - | 26.139 | 30.000 Pa
| 1684577 | Specific Loss | - | 130.6948 | 150.000 Pa
| 1684578 | Coefficient from ASHRAE Table | - | 0 | 0.000 Pa
| 1684581 | Specific Loss | - | 0.69704 | 0.800 Pa
| 1684583 | Coefficient from ASHRAE Table | - | 0 | 0.000 Pa
| 1684586 | Coefficient from ASHRAE Table | SD5-24 | 3.5746 | 4.103 Pa
199 | 722548 | Specific Loss | - | 0.30979 | 0.800 Pa | 259.819 Pa
| 722550 | Specific Loss | - | 0.30979 | 0.800 Pa
| 722554 | Specific Loss | - | 0.30979 | 0.800 Pa
| 722557 | Specific Loss | - | 58.0866 | 150.000 Pa
| 722558 | Specific Loss | - | 11.6173 | 30.000 Pa
| 722559 | Coefficient from ASHRAE Table | - | 0 | 0.000 Pa
| 722562 | Specific Loss | - | 0.30979 | 0.800 Pa
| 722596 | Coefficient from ASHRAE Table | SD5-24 | 29.6703 | 76.619 Pa
200 | 1713960 | Specific Loss | - | 0.4461 | 0.800 Pa | 202.356 Pa
| 1750957 | Specific Loss | - | 83.6446 | 150.000 Pa
| 1751007 | Specific Loss | - | 16.7289 | 30.000 Pa
| 1751027 | Specific Loss | - | 0.4461 | 0.800 Pa
| 1751088 | Coefficient from ASHRAE Table | SD5-24 | 11.1281 | 19.956 Pa
| 1751096 | Specific Loss | - | 0.4461 | 0.800 Pa
201 | 1607369 | Specific Loss | - | 130.6948 | 150.000 Pa | 183.425 Pa
| 1607370 | Specific Loss | - | 26.139 | 30.000 Pa
| 1607371 | Specific Loss | - | 0.69704 | 0.800 Pa
| 1607380 | Specific Loss | - | 0.69704 | 0.800 Pa
| 1607391 | Coefficient from ASHRAE Table | - | 0 | 0.000 Pa
| 2305722 | Coefficient from ASHRAE Table | SR5-11 | 1.5901 | 1.825 Pa
202 | 1607399 | Specific Loss | - | 130.6948 | 150.000 Pa | 184.815 Pa
| 1607400 | Specific Loss | - | 26.139 | 30.000 Pa
| 1607401 | Specific Loss | - | 0.69704 | 0.800 Pa
| 1607404 | Specific Loss | - | 0.69704 | 0.800 Pa
| 1607406 | Coefficient from ASHRAE Table | - | 0 | 0.000 Pa
| 2305576 | Coefficient from ASHRAE Table | SR5-11 | 2.8009 | 3.215 Pa
203 | 1607423 | Specific Loss | - | 130.6948 | 150.000 Pa | 187.002 Pa
| 1607424 | Specific Loss | - | 26.139 | 30.000 Pa
| 1607425 | Specific Loss | - | 0.69704 | 0.800 Pa
| 1607428 | Specific Loss | - | 0.69704 | 0.800 Pa
| 1607430 | Coefficient from ASHRAE Table | - | 0 | 0.000 Pa
| 2305538 | Coefficient from ASHRAE Table | SR5-11 | 4.7066 | 5.402 Pa
204 | 1607447 | Specific Loss | - | 130.6948 | 150.000 Pa | 181.600 Pa
| 1607448 | Specific Loss | - | 26.139 | 30.000 Pa
| 1607449 | Specific Loss | - | 0.69704 | 0.800 Pa
| 1607452 | Specific Loss | - | 0.69704 | 0.800 Pa
| 2305499 | Coefficient from ASHRAE Table | - | 0 | 0.000 Pa
205 | 460714 | Coefficient from ASHRAE Table | SD5-24 | 4.4 | 5.295 Pa | 6.895 Pa
| 460719 | Specific Loss | - | 0.66475 | 0.800 Pa
| 460724 | Coefficient from ASHRAE Table | - | 0 | 0.000 Pa
| 698807 | Specific Loss | - | 0.66475 | 0.800 Pa
206 | 460698 | Specific Loss | - | 0.16619 | 0.800 Pa | 74.880 Pa
| 460700 | Specific Loss | - | 0.16619 | 0.800 Pa
| 460704 | Coefficient from ASHRAE Table | - | 0 | 0.000 Pa
| 460707 | Coefficient from ASHRAE Table | CD6-4 | 0.24 | 1.155 Pa
| 460708 | Specific Loss | - | 6.232 | 30.000 Pa
| 460709 | Specific Loss | - | 0.16619 | 0.800 Pa
| 460714 | Coefficient from ASHRAE Table | SD5-24 | 0 | 0.000 Pa
| 460736 | Specific Loss | - | 0.16619 | 0.800 Pa
| 656434 | Coefficient from ASHRAE Table | SD5-24 | 8.4183 | 40.524 Pa
| 656441 | Coefficient from ASHRAE Table | - | 0 | 0.000 Pa
207 | 460714 | Coefficient from ASHRAE Table | SD5-24 | 21.8496 | 26.295 Pa | 27.895 Pa
| 460730 | Specific Loss | - | 0.66475 | 0.800 Pa
| 2304860 | Specific Loss | - | 0.66475 | 0.800 Pa
208 | 461433 | Specific Loss | - | 130.6948 | 150.000 Pa | 182.400 Pa
| 461441 | Coefficient from ASHRAE Table | - | 0 | 0.000 Pa
| 461443 | Specific Loss | - | 0.69704 | 0.800 Pa
| 1268753 | Specific Loss | - | 26.139 | 30.000 Pa
| 2500061 | Specific Loss | - | 0.69704 | 0.800 Pa
| 2500095 | Specific Loss | - | 0.69704 | 0.800 Pa
209 | 461441 | Coefficient from ASHRAE Table | - | 0 | 0.000 Pa | 0.000 Pa
| 2174425 | Coefficient from ASHRAE Table | - | 0 | 0.000 Pa